**C**. **मुख्य उत्पादक इकाइयों की अनुपलब्धता** Major Generating unit outages:

| **अनु क्रमांक**  **Sr. No** | **युनिट**  **Unit** | **संघटक**  **Constituent/**  **IPP** | **क्षमता Capacity**  **MW** | **से**  **From**  **समय दिनांक** | | **तक**  **To**  **समय दिनांक** | | **कारण**  **Reason** |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | **Time** | **Date** | **Time** | **Date** |  |
|  | VADINAR - UNIT 1 | Essar Mahan (EMPCL) | 600.0 | 08:18 | 16-09-2020 | Still out | Still out | BTL |
|  | Uran - UNIT 5 | Maharashtra | 108.0 | 06:18 | 16-09-2020 | 22:41 | 16-09-2020 | Turbine vibration high. |
|  | DGBP 3 - UNIT 1 | Gujarat | 375.0 | 05:43 | 16-09-2020 | 19:36 | 17-09-2020 | Due to non-availability of gas |
|  | SSP(RBPH) - UNIT 6 | SSP (SSNL) | 200.0 | 05:15 | 16-09-2020 | 11:15 | 16-09-2020 | Withdrawn as per schedule |
|  | SSP(RBPH) - UNIT 2 | SSP (SSNL) | 200.0 | 05:00 | 16-09-2020 | 10:15 | 16-09-2020 | Withdrawn as per schedule |
|  | DGBP 1 - UNIT 1 | Gujarat | 107.0 | 00:37 | 16-09-2020 | 13:23 | 16-09-2020 | RSD / RSD |
|  | KSTPS - UNIT 6 | NTPC | 500.0 | 21:04 | 15-09-2020 | 22:05 | 17-09-2020 | BTL |
|  | GSEG STG 2 - UNIT 1 | Gujarat | 351.0 | 20:45 | 15-09-2020 | 11:31 | 16-09-2020 | RSD / RSD |
|  | STPS - UNIT 4 | Gujarat | 250.0 | 17:48 | 15-09-2020 | 04:50 | 25-09-2020 | RSD / RSD |
|  | STPS - UNIT 3 | Gujarat | 250.0 | 15:38 | 15-09-2020 | 13:13 | 25-09-2020 | RSD / RSD |
|  | SSP(RBPH) - UNIT 2 | SSP (SSNL) | 200.0 | 13:15 | 15-09-2020 | 00:00 | 16-09-2020 | As per schedule |
|  | SSP(RBPH) - UNIT 5 | SSP (SSNL) | 200.0 | 13:00 | 15-09-2020 | 11:00 | 16-09-2020 | As per schedule |
|  | BECL - UNIT 1 | Gujarat | 250.0 | 06:52 | 15-09-2020 | 04:07 | 18-09-2020 | Coal feeding problem |
|  | SSP(RBPH) - UNIT 6 | SSP (SSNL) | 200.0 | 05:00 | 15-09-2020 | 00:00 | 16-09-2020 | As per schedule |
|  | SSP(RBPH) - UNIT 4 | SSP (SSNL) | 200.0 | 00:30 | 15-09-2020 | 10:45 | 16-09-2020 | As per schedule / As per schedule |
|  | Dhuvaran - UNIT 1 | Gujarat | 140.0 | 00:22 | 15-09-2020 | Still out | Still out | No Schedule / RSD. |
|  | DGBP 1 - UNIT 1 | Gujarat | 107.0 | 00:21 | 15-09-2020 | 16:50 | 15-09-2020 | RSD |
|  | SSP(RBPH) - UNIT 3 | SSP (SSNL) | 200.0 | 00:15 | 15-09-2020 | 10:30 | 16-09-2020 | As per schedule / As per schedule |
|  | Uran - UNIT 5 | Maharashtra | 108.0 | 00:09 | 15-09-2020 | 00:09 | 16-09-2020 | For filter replacement / For filter replacement |
|  | SSP(RBPH) - UNIT 1 | SSP (SSNL) | 200.0 | 00:00 | 15-09-2020 | Still out | Still out | As per schedule / As per schedule |
|  | SSP(RBPH) - UNIT 1 | SSP (SSNL) | 200.0 | 00:00 | 15-09-2020 | 10:00 | 16-09-2020 | As per schedule |
|  | PARLI - UNIT 8 | Maharashtra | 250.0 | 22:45 | 14-09-2020 | Still out | Still out | No Schedule / No schedule |
|  | Sanjay Gandhi TPS - UNIT 1 | Madhya Pradesh | 210.0 | 13:00 | 14-09-2020 | 16:01 | 14-09-2020 | Tripped on jerk during tripping of 220 KV BIRSINGHPUR-SGTPS CKT-2 due to B-ph earth fault. |
|  | PARLI - UNIT 7 | Maharashtra | 250.0 | 00:00 | 14-09-2020 | Still out | Still out | No Schedule / RSD. |
|  | Dhuvaran - UNIT 2 | Gujarat | 140.0 | 21:46 | 13-09-2020 | Still out | Still out | No Schedule / RSD. |
|  | DGBP 1 - UNIT 2 | Gujarat | 112.0 | 21:45 | 13-09-2020 | 14:30 | 16-09-2020 | RSD / RSD |
|  | DGBP 1 - UNIT 2 | Gujarat | 112.0 | 21:45 | 13-09-2020 | 16:35 | 14-09-2020 | No Schedule / RSD |
|  | BECL - UNIT 2 | Gujarat | 250.0 | 18:16 | 13-09-2020 | 11:17 | 17-09-2020 | Coal feeder problem. |
|  | Gandhinagar(GTPS) - UNIT 5 | Gujarat | 210.0 | 16:16 | 13-09-2020 | 04:15 | 25-09-2020 | RSD / RSD |
|  | Wanakbori - UNIT 3 | Gujarat | 210.0 | 16:15 | 13-09-2020 | 18:15 | 25-09-2020 | RSD / RSD |
|  | Wanakbori - UNIT 7 | Gujarat | 210.0 | 13:11 | 13-09-2020 | Still out | Still out | RSD / RSD |
|  | Wanakbori - UNIT 5 | Gujarat | 210.0 | 12:16 | 13-09-2020 | Still out | Still out | RSD / RSD |
|  | APL Mundra - UNIT 7 | Gujarat | 660.0 | 01:00 | 13-09-2020 | 09:30 | 18-09-2020 | Condenser tube leakage. |
|  | JPL Stg-I - UNIT 2 | Jindal power (JPL) | 250.0 | 00:00 | 13-09-2020 | 17:13 | 21-09-2020 | No Schedule / Low schedule. |
|  | DGBP 1 - UNIT 2 | Gujarat | 112.0 | 23:57 | 12-09-2020 | 17:52 | 13-09-2020 | RSD / RSD |
|  | GPPC - UNIT 1 | Gujarat | 351.0 | 23:45 | 12-09-2020 | 19:31 | 14-09-2020 | Non-availability of gas |
|  | APML Tiroda - UNIT 5 | ATIL-Adani | 660.0 | 20:54 | 12-09-2020 | 19:55 | 15-09-2020 | Tubine problem |
|  | UKAI - UNIT 3 | Gujarat | 200.0 | 16:53 | 12-09-2020 | 06:50 | 28-09-2020 | RSD / RSD |
|  | UKAI - UNIT 5 | Gujarat | 210.0 | 16:48 | 12-09-2020 | 18:56 | 27-09-2020 | RSD / RSD |
|  | TRN Energy - UNIT 1 | ACBIL | 300.0 | 15:22 | 12-09-2020 | Still out | Still out | Due to wet and poor coal quality. |
|  | Gandhinagar(GTPS) - UNIT 4 | Gujarat | 210.0 | 12:40 | 12-09-2020 | Still out | Still out | RSD / RSD |
|  | UTRAN STG II - UNIT 1 | Gujarat | 375.0 | 08:42 | 12-09-2020 | 04:56 | 14-09-2020 | During changeover activity of GTG from BUS B TO BUS A , Fire in Bus-A. All three isolator meltdown. |
|  | PARLI - UNIT 6 | Maharashtra | 250.0 | 00:00 | 12-09-2020 | Still out | Still out | No Schedule / Zero schedule |
|  | BECL - UNIT 2 | Gujarat | 250.0 | 23:28 | 11-09-2020 | 05:48 | 12-09-2020 | UAT problem |
|  | DGBP 1 - UNIT 2 | Gujarat | 112.0 | 21:26 | 11-09-2020 | 17:52 | 12-09-2020 | RSD / RSD |
|  | Wanakbori - UNIT 4 | Gujarat | 210.0 | 18:51 | 11-09-2020 | Still out | Still out | RSD / RSD |
|  | Wanakbori - UNIT 6 | Gujarat | 210.0 | 17:51 | 11-09-2020 | Still out | Still out | RSD / RSD |
|  | Marwa TPS - UNIT 1 | Chattisgarh | 500.0 | 09:44 | 11-09-2020 | 12:06 | 11-09-2020 | Tripped due to loss of fuel. |
|  | Solapur STPS - UNIT 2 | NTPC | 660.0 | 08:52 | 11-09-2020 | Still out | Still out | RSD / RSD |
|  | MB Power - UNIT 1 | Madhya Pradesh | 600.0 | 06:32 | 11-09-2020 | 08:59 | 14-09-2020 | APH Jamming. |
|  | DGBP 1 - UNIT 2 | Gujarat | 112.0 | 23:30 | 10-09-2020 | 16:03 | 11-09-2020 | RSD |
|  | DGBP 1 - UNIT 1 | Gujarat | 107.0 | 23:27 | 10-09-2020 | 16:35 | 14-09-2020 | RSD |
|  | KORBA(E) - UNIT 5 | Chattisgarh | 120.0 | 22:25 | 10-09-2020 | 04:23 | 12-09-2020 | Furnace draft pressure very high |
|  | GPPC - UNIT 2 | Gujarat | 351.0 | 10:30 | 10-09-2020 | 20:02 | 12-09-2020 | Tripped due to slip ring problem |
|  | UKAI - UNIT 5 | Gujarat | 210.0 | 06:06 | 10-09-2020 | 11:53 | 10-09-2020 | Due to flame failure |
|  | GSEG - UNIT 1 | Gujarat | 78.0 | 05:51 | 10-09-2020 | 17:19 | 16-09-2020 | Non availability of Gas |
|  | GSEG - UNIT 2 | Gujarat | 78.0 | 05:40 | 10-09-2020 | 12:46 | 16-09-2020 | Non availability of Gas |
|  | SSP(RBPH) - UNIT 2 | SSP (SSNL) | 200.0 | 05:15 | 10-09-2020 | 18:00 | 10-09-2020 | No Schedule / Withdrawn as per schedule |
|  | SSP(RBPH) - UNIT 3 | SSP (SSNL) | 200.0 | 05:15 | 10-09-2020 | 13:30 | 10-09-2020 | No Schedule / Withdrawn as per schedule |
|  | JP Nigrie - UNIT 1 | Jaypee Nigire (JNSTPP) | 660.0 | 02:10 | 10-09-2020 | 14:23 | 13-09-2020 | BTL |
|  | BECL - UNIT 1 | Gujarat | 250.0 | 23:31 | 09-09-2020 | 01:55 | 10-09-2020 | Flame failure |
|  | SSP(RBPH) - UNIT 6 | SSP (SSNL) | 200.0 | 23:30 | 09-09-2020 | 18:15 | 10-09-2020 | RSD / RSD |
|  | SSP(RBPH) - UNIT 5 | SSP (SSNL) | 200.0 | 23:15 | 09-09-2020 | 17:45 | 10-09-2020 | RSD / RSD |
|  | SSP(RBPH) - UNIT 1 | SSP (SSNL) | 200.0 | 23:00 | 09-09-2020 | 18:30 | 10-09-2020 | RSD / RSD |
|  | DGBP 3 - UNIT 1 | Gujarat | 375.0 | 19:13 | 09-09-2020 | 05:02 | 10-09-2020 | Tripped on vibration high |
|  | Jaigad - UNIT 3 | Maharashtra | 300.0 | 10:56 | 09-09-2020 | 11:13 | 30-09-2020 | CW duct leakages |
|  | UKAI - UNIT 4 | Gujarat | 200.0 | 08:15 | 09-09-2020 | 15:04 | 16-09-2020 | Coal feeding problem |
|  | JPL Stg-II - UNIT 4 | Jindal power (JPL) | 600.0 | 01:57 | 09-09-2020 | Still out | Still out | Coal Shortage / APH-B support brg. abnormal sound / coal shortage since 00:00hrs/24-09-2020 |
|  | Sasan - UNIT 5 | SASAN\_UMPP (SPL) | 660.0 | 19:45 | 08-09-2020 | 11:14 | 10-09-2020 | PA duct leakage |
|  | JPL Stg-II - UNIT 3 | Jindal power (JPL) | 600.0 | 04:00 | 08-09-2020 | Still out | Still out | Coal Shortage / Due to condenser tube leakage./ coal shortage w.e.f 00:00hrs of 12-09-2020 |
|  | REL - UNIT 1 | REL | 685.0 | 01:17 | 08-09-2020 | 16:10 | 21-09-2020 | Coal Shortage / Low coal stock |
|  | BECL - UNIT 2 | Gujarat | 250.0 | 17:38 | 07-09-2020 | 09:36 | 11-09-2020 | Coal feeding problem |
|  | SIPAT I - UNIT 2 | NTPC | 660.0 | 16:40 | 07-09-2020 | 04:12 | 10-09-2020 | Tripped on reheater temperature high. Kept out on BTL. |
|  | Gandhar - UNIT GT1 | NTPC | 144.3 | 22:01 | 05-09-2020 | 20:15 | 24-09-2020 | RSD / RSD. |
|  | Tarapur II - UNIT 1 | NPCIL | 540.0 | 07:00 | 05-09-2020 | Still out | Still out | urgent job in primary side |
|  | GIPCL STG 2 - UNIT 1 | GSECL | 165.0 | 22:58 | 04-09-2020 | Still out | Still out | withdrawn on RSD, converted to forced outage wef 08:00hrs/08-09-2020 for attending ACW line leakage |
|  | GADARWARA - UNIT 2 | NTPC | 800.0 | 18:37 | 04-09-2020 | Still out | Still out | Generator protection operated |
|  | Marwa TPS - UNIT 2 | Chattisgarh | 500.0 | 12:28 | 04-09-2020 | 16:27 | 18-09-2020 | clinker formation in bottom ash hopper |
|  | SLPP - UNIT 4 | Gujarat | 125.0 | 09:56 | 04-09-2020 | Still out | Still out | BTL |
|  | WANAKBORI GIS - UNIT 8 | Gujarat | 800.0 | 04:45 | 03-09-2020 | 17:15 | 15-09-2020 | BTL |
|  | APML Tiroda - UNIT 2 | ATIL-Adani | 660.0 | 19:41 | 01-09-2020 | 02:25 | 05-10-2020 | Tripped due to APH-2A hot PA bellow leakage |
|  | Khargone - UNIT 1 | NTPC | 660.0 | 16:00 | 29-08-2020 | 06:51 | 10-09-2020 | RSD / RSD. |
|  | Khargone - UNIT 2 | NTPC | 660.0 | 13:30 | 29-08-2020 | Still out | Still out | RSD / RSD. |
|  | ACBIL - UNIT 1 | ACBIL | 135.0 | 20:30 | 27-08-2020 | 17:00 | 29-09-2020 | due to all DCF choked |
|  | Chandrapur - UNIT 6 | Maharashtra | 500.0 | 10:55 | 27-08-2020 | 10:30 | 15-09-2020 | BTL |
|  | KAWAS - UNIT 2B | NTPC | 106.0 | 09:00 | 27-08-2020 | 17:29 | 20-09-2020 | Hot gas pass inspection |
|  | SCPL - UNIT 1 | ACBIL | 50.0 | 21:33 | 25-08-2020 | Still out | Still out | due to unavailability of usable coal stock |
|  | ALTPS - UNIT 2 | Gujarat | 125.0 | 18:30 | 24-08-2020 | 11:40 | 10-09-2020 | Tripped due to drum level disturbance |
|  | Singaji - UNIT 4 | Madhya Pradesh | 660.0 | 13:46 | 22-08-2020 | 14:39 | 11-09-2020 | RSD / RSD |
|  | KAWAS - UNIT 2A | NTPC | 106.0 | 06:10 | 22-08-2020 | Still out | Still out | RSD / Withdrawn after testing on Liquid fuel/RSD |
|  | GSEG STG 2 - UNIT 1 | Gujarat | 351.0 | 05:50 | 22-08-2020 | 11:10 | 15-09-2020 | Gas supply constraints; CONVERTED TO AOH SINCE 00:00HRS/28-08-2020 |
|  | Singaji - UNIT 2 | Madhya Pradesh | 600.0 | 16:00 | 21-08-2020 | 00:01 | 23-09-2020 | RSD / RSD |
|  | Jaigad - UNIT 4 | Maharashtra | 300.0 | 15:57 | 20-08-2020 | 08:34 | 11-09-2020 | AOH |
|  | Sanjay Gandhi TPS - UNIT 3 | Madhya Pradesh | 210.0 | 16:17 | 16-08-2020 | 23:35 | 30-09-2020 | RSD / RSD |
|  | Satpura II - UNIT 10 | Madhya Pradesh | 250.0 | 00:16 | 15-08-2020 | 12:16 | 15-09-2020 | AOH |
|  | Satpura II - UNIT 7 | Madhya Pradesh | 210.0 | 10:15 | 12-08-2020 | Still out | Still out | RSD / RSD |
|  | WPCL - UNIT 4 | Maharashtra | 135.0 | 00:45 | 12-08-2020 | Still out | Still out | No Schedule / No schedule |
|  | WPCL - UNIT 3 | Maharashtra | 135.0 | 00:45 | 12-08-2020 | Still out | Still out | No Schedule / No schedule |
|  | DGEN - UNIT 2 | Gujarat | 400.0 | 00:25 | 12-08-2020 | Still out | Still out | No Schedule / No schedule |
|  | Satpura II - UNIT 6 | Madhya Pradesh | 200.0 | 11:04 | 11-08-2020 | Still out | Still out | RSD / w/d on Reheater tube leakage, kept out on RSD since 21:00hrs/13-08-2020 |
|  | SLPP - UNIT 1 | Gujarat | 125.0 | 19:30 | 08-08-2020 | 20:39 | 14-09-2020 | AOH |
|  | SLPP - UNIT 1 | Gujarat | 125.0 | 19:30 | 08-08-2020 | 23:09 | 14-09-2020 | BTL |
|  | RKM Power - UNIT 3 | RKM | 360.0 | 16:34 | 08-08-2020 | Still out | Still out | RSD / As per schedule |
|  | Chandrapur - UNIT 7 | Maharashtra | 500.0 | 03:31 | 06-08-2020 | 20:57 | 28-09-2020 | Tripped due to sparking in the R phase generator winding |
|  | Singaji - UNIT 3 | Madhya Pradesh | 660.0 | 23:56 | 05-08-2020 | Still out | Still out | Tripped due to turbine vibration |
|  | ESSAR(Mahan) - UNIT 2 | Essar Mahan (EMPCL) | 600.0 | 05:25 | 03-08-2020 | Still out | Still out | Less Schedule / Withdrawn as per schedule. |
|  | Mouda II - UNIT 2 | NTPC | 660.0 | 21:00 | 02-08-2020 | Still out | Still out | RSD / RSD |
|  | JPL Stg-I - UNIT 1 | Jindal power (JPL) | 250.0 | 11:47 | 28-07-2020 | Still out | Still out | Electrical fault |
|  | KAWAS - UNIT 2C | NTPC | 116.1 | 02:51 | 15-07-2020 | 16:22 | 22-09-2020 | RSD / RSD |
|  | Tarapur I - UNIT 2 | NPCIL | 160.0 | 04:38 | 13-07-2020 | Still out | Still out | For cleaning of clogged basket strainer of cooling water system due to heavy ingress of debris from sea |
|  | Lara - UNIT 2 | NTPC | 800.0 | 06:16 | 12-07-2020 | 23:31 | 29-09-2020 | Trial operation completed at 01:00hrs |
|  | JP BINA - UNIT 1 | Madhya Pradesh | 250.0 | 23:56 | 02-07-2020 | Still out | Still out | RSD / w/d on BTL/later kept out on RSD |
|  | RGPPL - UNIT 3A | RGPPL | 332.0 | 22:34 | 02-07-2020 | Still out | Still out | Less gas; Unit Change over |
|  | Dahanu - UNIT 1 | Maharashtra | 250.0 | 23:55 | 27-06-2020 | 09:05 | 18-09-2020 | No Schedule / Zero schedule |
|  | DGEN - UNIT 3 | Gujarat | 400.0 | 00:25 | 22-06-2020 | Still out | Still out | No Schedule / no schedule |
|  | APML Tiroda - UNIT 5 | ATIL-Adani | 660.0 | 12:29 | 04-06-2020 | 04:29 | 11-09-2020 | RSD / RSD |
|  | URAN B0 - UNIT 1 | Maharashtra | 120.0 | 12:51 | 25-05-2020 | Still out | Still out | Shaft position trip |
|  | Uran - UNIT 7 | Maharashtra | 108.0 | 12:51 | 25-05-2020 | Still out | Still out | Shaft position issue |
|  | SKS Power - UNIT 1 | SKS | 300.0 | 15:48 | 13-05-2020 | Still out | Still out | No Schedule / w/d on BTL/ kept out on No schedule later |
|  | DGEN - UNIT 1 | Gujarat | 400.0 | 00:26 | 23-04-2020 | Still out | Still out | No Schedule / no schedule |
|  | TROMBAY - UNIT 8 | Maharashtra | 200.0 | 16:55 | 11-04-2020 | Still out | Still out | No Schedule / No scheule |
|  | NASIK - UNIT 4 | Maharashtra | 210.0 | 19:47 | 25-03-2020 | Still out | Still out | RSD / Low schedule |
|  | RGPPL - UNIT 3B | RGPPL | 332.0 | 00:10 | 23-03-2020 | Still out | Still out | RSD / Les requisition |
|  | Wanakbori - UNIT 7 | Gujarat | 210.0 | 11:25 | 22-03-2020 | 14:22 | 10-09-2020 | Low schedule |
|  | Gandhinagar(GTPS) - UNIT 4 | Gujarat | 210.0 | 08:41 | 22-03-2020 | 04:15 | 10-09-2020 | Low schedule |
|  | Gandhinagar(GTPS) - UNIT 3 | Gujarat | 210.0 | 08:24 | 22-03-2020 | Still out | Still out | Low schedule |
|  | Wanakbori - UNIT 5 | Gujarat | 210.0 | 08:02 | 22-03-2020 | 11:35 | 10-09-2020 | Low schedule |
|  | Wanakbori - UNIT 6 | Gujarat | 210.0 | 14:25 | 20-03-2020 | 09:27 | 10-09-2020 | RSD / Low schedule |
|  | Wanakbori - UNIT 1 | Gujarat | 210.0 | 11:05 | 20-03-2020 | Still out | Still out | RSD / Low schedule / RSD |
|  | Wanakbori - UNIT 2 | Gujarat | 210.0 | 19:01 | 18-03-2020 | Still out | Still out | RSD / w/d for replacement of LPT differential sensor. /Converted to RSD since 11:05hrs/20-03-2020 |
|  | RGPPL - UNIT 2A | RGPPL | 332.0 | 19:52 | 12-03-2020 | Still out | Still out | less gas; unit changeover |
|  | RATTAN INDIA POWER (A) - UNIT 2 | Rattan India (RIPL) | 270.0 | 20:15 | 09-03-2020 | Still out | Still out | No Schedule / Zero Schedule |
|  | RATTAN INDIA POWER (A) - UNIT 1 | Rattan India (RIPL) | 270.0 | 19:30 | 04-03-2020 | Still out | Still out | No Schedule / Zero schedule |
|  | Uran - UNIT 8 | Maharashtra | 108.0 | 20:57 | 01-03-2020 | Still out | Still out | Gas shortage |
|  | Satpura II - UNIT 3 | Madhya Pradesh | 210.0 | 23:54 | 29-02-2020 | Still out | Still out | RSD / Low schedule |
|  | Satpura II - UNIT 4 | Madhya Pradesh | 210.0 | 02:52 | 22-02-2020 | Still out | Still out | BTL |
|  | NASIK - UNIT 3 | Maharashtra | 210.0 | 00:00 | 17-02-2020 | Still out | Still out | CW Pump high vibration |
|  | RATTAN INDIA POWER (A) - UNIT 5 | Rattan India (RIPL) | 270.0 | 19:30 | 11-02-2020 | Still out | Still out | No Schedule / Zero schedule |
|  | RATTAN INDIA POWER (A) - UNIT 3 | Rattan India (RIPL) | 270.0 | 18:00 | 11-02-2020 | Still out | Still out | No Schedule / Zero Schedule |
|  | Tarapur I - UNIT 1 | NPCIL | 160.0 | 10:37 | 08-01-2020 | Still out | Still out | Refueling |
|  | NASIK - UNIT 5 | Maharashtra | 210.0 | 10:25 | 12-12-2019 | Still out | Still out | PA Fan problem (Under Case 4 Bidding from 04.25Hrs DT. 13-12-2019) |
|  | RATTAN INDIA POWER (A) - UNIT 4 | Rattan India (RIPL) | 270.0 | 00:00 | 12-11-2019 | Still out | Still out | No Schedule / Zero schedule |
|  | Koradi - UNIT 7 | Maharashtra | 210.0 | 20:00 | 12-09-2019 | Still out | Still out | No Schedule / Zero schedule |
|  | Koradi - UNIT 6 | Maharashtra | 210.0 | 15:41 | 06-09-2019 | Still out | Still out | RSD / Low schedule |
|  | Bhusawal - UNIT 3 | Maharashtra | 210.0 | 17:56 | 01-09-2019 | Still out | Still out | RSD / As per schedule |
|  | GPEC - UNIT 3 | Gujarat | 138.0 | 22:02 | 20-07-2019 | Still out | Still out | As per schedule |
|  | RKM Power - UNIT 4 | RKM | 360.0 | 00:00 | 20-03-2019 | Still out | Still out | No Schedule / Commercial operation declared from 00:00hrs of 20-03-2019; kept out on less fuel; intimated that from 10-05-2019, the reason is no schedule due to no PPA |
|  | VIPL - UNIT 2 | Maharashtra | 300.0 | 00:15 | 17-01-2019 | Still out | Still out | Coal Shortage / Coal shortage |
|  | VIPL - UNIT 1 | Maharashtra | 300.0 | 00:30 | 29-12-2018 | Still out | Still out | Coal Shortage / Coal shortage |
|  | GPEC - UNIT 2 | Gujarat | 138.0 | 12:34 | 10-12-2018 | Still out | Still out | RSD / No PPA zero schedule |
|  | GPEC - UNIT 4 | Gujarat | 241.0 | 16:36 | 06-12-2018 | Still out | Still out | High pressure control valve problem |
|  | WPCL - UNIT 1 | Maharashtra | 135.0 | 04:48 | 25-11-2018 | Still out | Still out | No PPA |
|  | KORBA(E) - UNIT 4 | Chattisgarh | 50.0 | 15:46 | 14-09-2018 | Still out | Still out | Outage of coal mill |
|  | KORBA(E) - UNIT 3 | Chattisgarh | 50.0 | 12:42 | 12-09-2018 | Still out | Still out | Super heater problem |
|  | IEPL - UNIT 1 | IEPL | 270.0 | 21:26 | 28-08-2018 | Still out | Still out | Coal Shortage / Coal shortage |
|  | KORBA(E) - UNIT 2 | Chattisgarh | 50.0 | 20:53 | 23-10-2017 | Still out | Still out | Mill fan problem |
|  | KORBA(E) - UNIT 1 | Chattisgarh | 50.0 | 21:46 | 06-08-2017 | Still out | Still out | Water wall tube leakage |
|  | PIONEER(262+127) - UNIT 1 | Maharashtra | 388.0 | 17:45 | 07-02-2017 | Still out | Still out | RSD / As per schedule |
|  | TROMBAY - UNIT 6 | Maharashtra | 500.0 | 00:00 | 04-05-2016 | Still out | Still out | Unit 6 is kept under economic shutdown since 4th May. |
|  | PARLI - UNIT 5 | Maharashtra | 210.0 | 14:55 | 06-07-2015 | Still out | Still out | ECONOMIC SHUT DOWN SINCE 1ST APRIL 2016 |
|  | PARLI - UNIT 4 | Maharashtra | 210.0 | 18:45 | 05-07-2015 | Still out | Still out | ECONOMIC SHUT DOWN SINCE 1ST APRIL 2016 |
|  | RGPPL - UNIT 1A | RGPPL | 320.0 | 13:30 | 08-07-2014 | Still out | Still out | Gas shortage |
|  | RGPPL - UNIT 1B | RGPPL | 320.0 | 23:00 | 31-03-2014 | Still out | Still out | Gas shortage |

**Note: Units out for more than 72 hrs are only included.**

**मुख्य पारागमन की अनुपलब्धता** Major Transmission element outages

| **अनु क्रमांक**  **Sr. No** | **युनिट**  Unit | **संघटक**  Constituent/ IPP | **क्षमता**  kV | **से**  From  **समय दिनांक** | | **तक**  To  **समय दिनांक** | | **कारण**  Reason |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | **Time** | **Date** | **Time** | **Date** |  |
|  | 400KV-AMRELI-HADALA-1 | Gujarat | 400KV | 23:41 | 16-09-2020 | 08:20 | 17-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-RANCHODPURA-CHORANIA-2 | WTGL-Adani | 400KV | 23:39 | 16-09-2020 | 08:24 | 17-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KARAD-JAIGAD-2 | Maharashtra | 400KV | 23:34 | 16-09-2020 | 19:03 | 27-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KOYNA STAGE IV-LONIKHAND-1 | Maharashtra | 400KV | 23:30 | 16-09-2020 | 11:01 | 17-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-DHULE-MS-BABLESHWAR-2 | Maharashtra | 400KV | 23:30 | 16-09-2020 | 06:36 | 17-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 23:24 | 16-09-2020 | 09:19 | 17-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-PADGHE-NAGOTHANE-2 | Maharashtra | 400KV | 20:00 | 16-09-2020 | 10:55 | 18-09-2020 | Manually opened due to High Voltage / MOHV |
|  | HVDC 800KV Raigarh-GIS-HVDC Pole 2 | POWERGRID-WR1 (PGCIL) | 800KV | 18:20 | 16-09-2020 | 08:51 | 17-09-2020 | Blocked after completion of testing |
|  | 400KV/220KV HADALA-ICT-4 | Gujarat | 400KV/220KV | 17:51 | 16-09-2020 | 17:32 | 17-09-2020 | R-phase LA blast at LV side; also 220kV Rajkot-2 feeder tripped |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 17:49 | 16-09-2020 | 06:42 | 17-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-DHULE-DHULE-MS-2 | BDTCL-Sterlite | 400KV | 17:23 | 16-09-2020 | 18:32 | 16-09-2020 | Line tripped on DT received at Dhule MH. No relay indication at BDTCL Dhule end. |
|  | 400KV-VELODA-CHARANKA-1 | Gujarat | 400KV | 16:51 | 16-09-2020 | 18:00 | 16-09-2020 | Line tripped on R ph fault. Charanka End:Z1, 3.7kA, 61.4km. From Veloda end: 9.9 kA, |
|  | GWALIOR - 400KV - Bus 2 | POWERGRID-WR2 (PGCIL) | 400KV | 15:59 | 16-09-2020 | 19:14 | 16-09-2020 | To attained Hot spot in B-phase isolator of 413 Bay (Main Bay of 400/220/33kV ICT-3). |
|  | 400KV/220KV GWALIOR-ICT-1 | POWERGRID-WR2 (PGCIL) | 400KV/220KV | 15:39 | 16-09-2020 | 17:19 | 16-09-2020 | sparking on isolator of Tie bay, Main bay is under open condition due to bus outage |
|  | EKTUNI - 765KV - Bus 2 | Maharashtra | 765KV | 12:10 | 16-09-2020 | 18:44 | 16-09-2020 | For AMP works |
|  | 765KV-AKOLA (2)-EKTUNI-1 | MEGPTCL | 765KV | 12:02 | 16-09-2020 | 13:08 | 16-09-2020 | Tripped at Akola end only while availing Bus 2 outage at Ektuni. DT received at Akola. |
|  | PUNE-PG - 400KV - Bus 1 | POWERGRID-WR1 (PGCIL) | 400KV | 11:24 | 16-09-2020 | 19:16 | 16-09-2020 | For AMP works |
|  | SHUJALPUR - 400KV - Bus 2 | POWERGRID-WR2 (PGCIL) | 400KV | 11:08 | 16-09-2020 | 18:40 | 16-09-2020 | To attend bus side isolator sparking problem |
|  | 132KV-VSTPS-WAIDHAN-2 | Madhya Pradesh,NTPC | 132KV | 10:54 | 16-09-2020 | 10:46 | 17-09-2020 | For hot point Attending work. |
|  | BIRSINGPUR - 400KV - Bus 1 | Madhya Pradesh | 400KV | 10:49 | 16-09-2020 | 14:39 | 16-09-2020 | For replacement of faulty insulator string |
|  | Tie Bay - 765KV-AURANGABAD-PADGHE-PG-2 AND FUTURE | POWERGRID-WR1 (PGCIL) | 765KV | 10:36 | 16-09-2020 | 15:18 | 16-09-2020 | For AMP works |
|  | 400KV/220KV BINA-MP-ICT-1 | Madhya Pradesh | 400KV/220KV | 10:36 | 16-09-2020 | 20:51 | 19-09-2020 | For 400KV side HCB Isolator replacement work. |
|  | 400KV-PARLI-M-SOLAPUR-M-1 | Maharashtra | 400KV | 10:06 | 16-09-2020 | 19:43 | 16-09-2020 | For AMP works |
|  | 400KV/220KV INDORE-MP-ICT-4 | Madhya Pradesh | 400KV/220KV | 10:03 | 16-09-2020 | 17:27 | 16-09-2020 | Maintenance |
|  | INDORE - 765KV B/R 1 | POWERGRID-WR2 (PGCIL) | 765KV | 09:58 | 16-09-2020 | 02:34 | 21-09-2020 | Voltage Regulation / VR |
|  | Tie Bay - 765KV/400KV INDORE-ICT-1 AND INDORE - 765KV B/R 1 | POWERGRID-WR2 (PGCIL) | 765KV | 09:57 | 16-09-2020 | 19:55 | 19-09-2020 | Breaker could not be taken in service after taking out BR due to PD alarm. |
|  | 400KV/220KV KHAPARKHEDA-ICT-2 | Maharashtra | 400KV/220KV | 09:49 | 16-09-2020 | 17:00 | 16-09-2020 | Testing work |
|  | RAIGARH-PS - 765KV B/R 1 | POWERGRID-WR1 (PGCIL) | 765KV | 09:43 | 16-09-2020 | 18:00 | 16-09-2020 | AMP |
|  | 400KV-ESSAR MAHAN-BILASPUR-1 L/R@ ESSAR MAHAN - 400KV | Essar Mahan (EMPCL) | 400KV | 09:36 | 16-09-2020 | 14:19 | 16-09-2020 | For AMP works |
|  | Tie Bay - 765KV-Solapur-Raichur-2 AND FUTURE | POWERGRID-WR1 (PGCIL) | 765KV | 09:34 | 16-09-2020 | 17:51 | 16-09-2020 | For AMP works |
|  | 765KV-PUNE-PG-Solapur-1 L/R@ Solapur - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 09:34 | 16-09-2020 | 09:45 | 16-09-2020 | LR taken as BR. |
|  | 765KV-Pune-GIS-Solapur-1 | POWERGRID-WR1 (PGCIL) | 765KV | 09:34 | 16-09-2020 | 09:57 | 19-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 765KV-PUNE-PG-Solapur-1 L/R@ PUNE-PG - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 09:34 | 16-09-2020 | 10:05 | 16-09-2020 | LR taken as BR. |
|  | 220KV-KHANDWA-CHHANERA-2 | Madhya Pradesh | 220KV | 09:27 | 16-09-2020 | 17:49 | 16-09-2020 | For line maintenance work. |
|  | 400KV-BHOPAL-MP-BINA-MP-2 | Madhya Pradesh | 400KV | 09:27 | 16-09-2020 | 18:38 | 16-09-2020 | For line maintenance work. |
|  | 400KV/220KV NAGDA-ICT-2 | Madhya Pradesh | 400KV/220KV | 09:16 | 16-09-2020 | 16:31 | 16-09-2020 | To attend NIFES alarm |
|  | 220KV-VAPI-GUJARAT-KAKRAPAR 1&2-1 | Gujarat | 220KV | 08:48 | 16-09-2020 | 13:28 | 16-09-2020 | to attend hot spot at VAPI s/s end. |
|  | KORADI-III - 765KV B/R 1 | MEGPTCL | 765KV | 08:48 | 16-09-2020 | 23:41 | 16-09-2020 | Voltage Regulation / VR. |
|  | 765KV-BINA-JABALPUR-3 | JTCL-Sterlite | 765KV | 08:18 | 16-09-2020 | 18:42 | 16-09-2020 | A/R Non Auto / A/R In non-Auto Mode forEarthwire / OPGW Rectification work. |
|  | 765KV-BINA-GWALIOR-2 | POWERGRID-WR2 (PGCIL) | 765KV | 08:16 | 16-09-2020 | 18:38 | 16-09-2020 | A/R Non Auto / A/R OFF for Tower Strengthening works |
|  | 400KV/220KV RANCHODPURA-ICT-1 | Gujarat | 400KV/220KV | 08:02 | 16-09-2020 | 17:43 | 16-09-2020 | Maintenance |
|  | 765KV-DHARAMJAYGARH-RANCHI-1 | POWERGRID-ER,POWERGRID-WR1 (PGCIL) | 765KV | 08:00 | 16-09-2020 | 19:14 | 16-09-2020 | For Tower Strengthning work. |
|  | 400KV-RANCHODPURA-KANSARI-1 | WTGL-Adani | 400KV | 03:25 | 16-09-2020 | 07:29 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-RANCHODPURA-CHORANIA-2 | WTGL-Adani | 400KV | 03:23 | 16-09-2020 | 07:25 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-AMRELI-HADALA-1 | Gujarat | 400KV | 03:23 | 16-09-2020 | 07:26 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-SUGEN-PIRANA-T-2 | Torrent Power (TPL) | 400KV | 03:22 | 16-09-2020 | 07:28 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KOYNA STAGE IV-LONIKHAND-1 | Maharashtra | 400KV | 00:10 | 16-09-2020 | 07:40 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 765KV-AURANGABAD-Solapur-2 L/R@ AURANGABAD - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 22:10 | 15-09-2020 | 22:27 | 15-09-2020 | Voltage Regulation / VR |
|  | 765KV-AURANGABAD-Solapur-2 L/R@ Solapur - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 22:10 | 15-09-2020 | 22:16 | 15-09-2020 | Voltage Regulation / VR |
|  | 765KV-AURANGABAD-Solapur-2 | POWERGRID-WR1 (PGCIL) | 765KV | 22:10 | 15-09-2020 | 10:29 | 23-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 19:55 | 15-09-2020 | 07:58 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-PADGHE-NAGOTHANE-1 | Maharashtra | 400KV | 19:33 | 15-09-2020 | 09:29 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 765KV-SASAN-SATNA-2 | POWERGRID-WR2 (PGCIL) | 765KV | 19:16 | 15-09-2020 | 19:17 | 15-09-2020 | Line autoreclosed on Y ph fault.From Sasan end: Z1, 5.8 kA, 97.3 km |
|  | 400KV-VINDHYACHAL-JABALPUR-2 | POWERGRID-WR2 (PGCIL) | 400KV | 18:49 | 15-09-2020 | 18:50 | 15-09-2020 | Y-phase A/R successful. V'chal end:Fault current-1.45 Kamp,Dist-275 KM. Jabalpur end:Fault current-1.5 Kamp,Dist-2204 KM. |
|  | 400KV-VINDHYACHAL-JABALPUR-1 | POWERGRID-WR2 (PGCIL) | 400KV | 18:49 | 15-09-2020 | 18:50 | 15-09-2020 | Y-phase A/R successful. V'chal end:Fault current-1.48 Kamp,Dist-268 KM. Jabalpur end:Fault current-1.5 Kamp,Dist-220.8 KM. |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 18:27 | 15-09-2020 | 08:15 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KARAD-JAIGAD-1 | Maharashtra | 400KV | 18:26 | 15-09-2020 | 07:45 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 220KV-BACHAU-Charadvada-2 | Gujarat | 220KV | 17:18 | 15-09-2020 | 17:55 | 15-09-2020 | Line tripped on R phase to earth fault,In Bachhau end ,Fault current-2.2 Kamp,Dist-124.4 KM.In Charwada end,Fault ciurrent-3.17 Kamp,Dist-37.1 KM. |
|  | 400KV/220KV NEW KOYNA-ICT-2 | Maharashtra | 400KV/220KV | 17:03 | 15-09-2020 | 19:21 | 15-09-2020 | To attend hotspot in R phase CT |
|  | SHUJALPUR - 400KV B/R 1 | POWERGRID-WR2 (PGCIL) | 400KV | 16:42 | 15-09-2020 | 19:51 | 15-09-2020 | Hand tripped due to heavy sparking in isolator |
|  | 400KV-JABALPUR-PS-MB POWER-1 | POWERGRID-WR2 (PGCIL) | 400KV | 15:56 | 15-09-2020 | 16:20 | 15-09-2020 | Line tripped on B phase to earth fault. Fault current-2.67 Kamp,Dist-154.15 Km. |
|  | 400KV-Wardha-AKOLA-2 | POWERGRID-WR1 (PGCIL) | 400KV | 15:36 | 15-09-2020 | 15:37 | 15-09-2020 | Voltage Regulation / line tripped on Y phase earth fault,zone-1.In Wardha end fault current-6.6 Kamp,Dist-56 KM,In Akola end,Fault current-3.42 Kamp,Dist-100.1 KM |
|  | 400KV-NAGDA-SHUJALPUR-2 | POWERGRID-WR2 (PGCIL) | 400KV | 14:49 | 15-09-2020 | 19:50 | 15-09-2020 | To attend hot spot observed at middle phase jumper ( Gantry side ) |
|  | Damoh - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 13:37 | 15-09-2020 | 19:41 | 15-09-2020 | For attending the zero current through y-ph of the main bay 413 |
|  | EKTUNI - 400KV - Bus 2 | Maharashtra | 400KV | 13:04 | 15-09-2020 | 16:42 | 15-09-2020 | For AMP works |
|  | 220KV-RAIGARH-BUDHIPADAR | Chattisgarh | 220KV | 12:50 | 15-09-2020 | 14:47 | 15-09-2020 | Line tripped on B phase to earth fault,fault current-2.2 Kamp,Dist-57.6 KM. |
|  | 220KV-MORENA-MORENA-MP-1 | Madhya Pradesh | 220KV | 12:26 | 15-09-2020 | 19:31 | 15-09-2020 | For line maintenance work. |
|  | 400KV/220KV Bhuj-ICT-3 | POWERGRID-WR2 (PGCIL) | 400KV/220KV | 12:22 | 15-09-2020 | 12:23 | 15-09-2020 | ICT-3 first time synchronized from 220 kV side at 12:23 hrs. |
|  | 400KV-BHOPAL-MP-BINA-MP-1 | Madhya Pradesh | 400KV | 11:28 | 15-09-2020 | 18:17 | 15-09-2020 | For line maintenance work. |
|  | 220KV-XELDEM-AMBEWADI-1 | GOA (GED) | 220KV | 11:22 | 15-09-2020 | 11:59 | 15-09-2020 | Line Tripped on B- Phase to earth fault Zone-1,Dist= 23.03 Km,Fault Current= 2.358 KA |
|  | 400KV-Aurangabad-M (Waluj)-DEEPNAGAR-1 | Maharashtra | 400KV | 11:17 | 15-09-2020 | 12:51 | 15-09-2020 | 89-C b-phase isolator hotspot |
|  | ALKUD - 400KV - Bus 1 | Maharashtra | 400KV | 11:08 | 15-09-2020 | 13:02 | 15-09-2020 | Quarterly maintenance work. |
|  | Main Bay - 765KV-AURANGABAD-PADGHE-PG-2 AND PADGHE-PG - 765KV - Bus 2 | POWERGRID-WR1 (PGCIL) | 765KV | 10:56 | 15-09-2020 | 16:39 | 15-09-2020 | For AMP works |
|  | 765KV-AURANGABAD-Solapur-1 | POWERGRID-WR1 (PGCIL) | 765KV | 10:54 | 15-09-2020 | 20:19 | 15-09-2020 | To facilitate SLR outage at Aurangabad end, |
|  | 765KV-AURANGABAD-Solapur-1 L/R@ AURANGABAD - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 10:54 | 15-09-2020 | 20:19 | 15-09-2020 | To facilitate SLR at Aurangabad end. |
|  | 400KV-RGPPL-NAGOTHANE-2 | Maharashtra | 400KV | 10:35 | 15-09-2020 | 15:05 | 15-09-2020 | For urgent removing slipped earth wire at loc. no 293 |
|  | 765KV/400KV Pune-GIS-ICT-1 | POWERGRID-WR1 (PGCIL) | 765KV/400KV | 10:35 | 15-09-2020 | 05:10 | 16-09-2020 | For AMP works. |
|  | 220KV-KHANDWA-CHHANERA-1 | Madhya Pradesh | 220KV | 10:17 | 15-09-2020 | 17:03 | 15-09-2020 | For line maintenance work. |
|  | 400KV/220KV INDORE-MP-ICT-1 | Madhya Pradesh | 400KV/220KV | 10:10 | 15-09-2020 | 18:27 | 15-09-2020 | for Post-monsoon maintenance work. |
|  | 765KV/400KV SEONI-ICT-3 | POWERGRID-WR1 (PGCIL) | 765KV/400KV | 10:04 | 15-09-2020 | 19:23 | 15-09-2020 | For AMP Works. |
|  | CHAMPA - 765KV - Bus 2 | POWERGRID-WR1 (PGCIL) | 765KV | 09:40 | 15-09-2020 | 19:59 | 15-09-2020 | 765KV B/R-2 AUXILLIARY BUS IPS TUBE BPI ERRECTION WORK |
|  | Main Bay - 765KV-BHOPAL-INDORE-1 AND INDORE - 765KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 765KV | 09:30 | 15-09-2020 | 17:49 | 15-09-2020 | For AMP works |
|  | 220KV-VYANKATPURA-VADODARA-1 | Gujarat | 220KV | 09:27 | 15-09-2020 | 17:06 | 15-09-2020 | For AMP works |
|  | 400KV-SIPAT-RAIPUR-1 | POWERGRID-WR1 (PGCIL) | 400KV | 09:08 | 15-09-2020 | 20:32 | 15-09-2020 | AMP works |
|  | 765KV-BINA-JABALPUR-3 | JTCL-Sterlite | 765KV | 08:32 | 15-09-2020 | 18:29 | 15-09-2020 | A/R Non Auto / for Earthwire / OPGW Rectification work |
|  | 400KV-HADALA-VARSANA-1 | Gujarat | 400KV | 08:30 | 15-09-2020 | 15:16 | 15-09-2020 | For PG Isolator maintanance work and feeder bay maint work and line maintenance work. |
|  | 400KV-DEHGAM-PIRANA-1 | POWERGRID-WR2 (PGCIL) | 400KV | 08:20 | 15-09-2020 | 17:47 | 02-10-2020 | For Transmission Line diversion work due to Bullet train. |
|  | 400KV/220KV JETPUR-ICT-4 | Gujarat | 400KV/220KV | 08:16 | 15-09-2020 | 11:00 | 15-09-2020 | To provide HT cap on Bushing |
|  | 400KV-PIRANA-NICOL-II-1 | POWERGRID-WR2 (PGCIL) | 400KV | 08:11 | 15-09-2020 | 17:52 | 02-10-2020 | For Transmission Line diversion work due to Bullet train |
|  | 765KV-DHARAMJAYGARH-RANCHI-1 | POWERGRID-ER,POWERGRID-WR1 (PGCIL) | 765KV | 08:06 | 15-09-2020 | 20:55 | 15-09-2020 | For Tower Strengthning work |
|  | 765KV-SATNA-Vindhyachal(PS)-1 | POWERGRID-WR2 (PGCIL) | 765KV | 08:02 | 15-09-2020 | 20:39 | 16-09-2020 | For power line crossing works of 765kV Vindhyachal-Varansi T/L by Vindhyachal TLC. |
|  | 765KV-BINA-GWALIOR-2 | POWERGRID-WR2 (PGCIL) | 765KV | 07:39 | 15-09-2020 | 19:43 | 15-09-2020 | A/R Non Auto / A/R OFF for Tower Strengthening works. |
|  | 132KV-Kirnapur-DONGARGARH-1 | Chattisgarh,Madhya Pradesh | 132KV | 05:00 | 15-09-2020 | 05:32 | 15-09-2020 | Tripped on Y-E fault / Zone -1, 2.47 km, 6.4 kA from Kirnapur, 73.2 km, 1.09.kA from Dongargarh |
|  | 400KV-TARAPUR 34-PADGHE-1 | POWERGRID-WR2 (PGCIL) | 400KV | 02:56 | 15-09-2020 | 08:47 | 15-09-2020 | Tripped on High voltage / High voltage |
|  | 400KV-RANCHODPURA-CHORANIA-2 | WTGL-Adani | 400KV | 01:53 | 15-09-2020 | 07:51 | 15-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-AMRELI-HADALA-1 | Gujarat | 400KV | 01:52 | 15-09-2020 | 07:49 | 15-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-RANCHODPURA-KANSARI-2 | WTGL-Adani | 400KV | 01:51 | 15-09-2020 | 08:41 | 15-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-SUGEN-PIRANA-T-2 | Torrent Power (TPL) | 400KV | 01:50 | 15-09-2020 | 07:52 | 15-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 765KV-Wardha-RAIPUR-PS (DURG)-1 | POWERGRID-WR1 (PGCIL) | 765KV | 01:46 | 15-09-2020 | Still out | Still out | Manually opened due to High Voltage / High voltage |
|  | 765KV-Wardha-RAIPUR-PS (DURG)-1 L/R@ RAIPUR-PS (DURG) - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 01:46 | 15-09-2020 | 02:15 | 15-09-2020 | On voltage regulation |
|  | 400KV-SOJA-WANAKBORI-GIS-1 | Gujarat | 400KV | 01:30 | 15-09-2020 | 07:36 | 24-09-2020 | MOHV |
|  | 400KV-SOJA-WANAKBORI-GIS-2 | Gujarat | 400KV | 01:30 | 15-09-2020 | 07:35 | 24-09-2020 | MOHV |
|  | HVDC 500KV VINDHYACHAL Pole 2 | POWERGRID-WR2 (PGCIL) | 500KV | 00:58 | 15-09-2020 | 08:00 | 15-09-2020 | Blocked due to Thyristor Failure Level 2 alarm |
|  | 400KV-KOYNA STAGE IV-LONIKHAND-1 | Maharashtra | 400KV | 22:10 | 14-09-2020 | 07:53 | 15-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 22:07 | 14-09-2020 | 08:02 | 15-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-RAJGARH-KASOR-2 FSC@ RAJGARH | POWERGRID-WR2 (PGCIL) | 400KV | 21:53 | 14-09-2020 | 14:50 | 22-09-2020 | Voltage Regulation / Voltage Regulation |
|  | 400KV-RAJGARH-KASOR-1 FSC@ RAJGARH | POWERGRID-WR2 (PGCIL) | 400KV | 21:52 | 14-09-2020 | 14:46 | 22-09-2020 | Voltage Regulation / Voltage Regulation |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 18:15 | 14-09-2020 | 08:04 | 15-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV/220KV KOLHAPUR-ICT-3 | Maharashtra | 400KV/220KV | 17:58 | 14-09-2020 | 18:14 | 14-09-2020 | For restoration of 220kV B Bus, as working spring of 220kV D Isolator R ph broken. |
|  | 400KV-BHUJ-CGPL-2 | POWERGRID-WR2 (PGCIL) | 400KV | 15:19 | 14-09-2020 | 15:20 | 14-09-2020 | R-E Fault. A/R Successful |
|  | HVDC 800KV Raigarh-GIS-HVDC Pole 1 | POWERGRID-WR1 (PGCIL) | 800KV | 15:14 | 14-09-2020 | 17:14 | 14-09-2020 | DC voltage divider giving erroneous values intermittently |
|  | 765KV-DHULE-KHANDWA-2 L/R@ KHANDWA-PS - 765KV | KTL-Sterlite | 765KV | 14:34 | 14-09-2020 | 16:04 | 14-09-2020 | Fire Detector Trip alarm in the NIFPS panel of R-Phase Line Reactor |
|  | 220KV-Damoh-SAGAR-2 | Madhya Pradesh | 220KV | 14:30 | 14-09-2020 | 15:13 | 14-09-2020 | B phase fault tripped from Damoh end only |
|  | BIRSINGPUR - 400KV - Bus 2 | Madhya Pradesh | 400KV | 13:17 | 14-09-2020 | 18:31 | 14-09-2020 | Replacement of faulty disc insulator string |
|  | 400KV-BIRSINGPUR-KATNI-1 | Madhya Pradesh | 400KV | 12:41 | 14-09-2020 | 18:35 | 14-09-2020 | Replacement of faulty disc insulator string |
|  | 400KV-KORBA-NTPC-BIRSINGPUR-2 | POWERGRID-WR1 (PGCIL) | 400KV | 12:38 | 14-09-2020 | 19:12 | 14-09-2020 | Bus Isolator jammed required maintenance |
|  | INDORE - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 12:34 | 14-09-2020 | 18:23 | 14-09-2020 | To replace spider and Auxiliary contact |
|  | 400KV-ALKUD-Solapur-1 | WTPL-Adani | 400KV | 11:49 | 14-09-2020 | 17:29 | 14-09-2020 | Q.M work diagnostic testing work |
|  | 220KV-SEONI-PG-CHINDWARA-1 | Madhya Pradesh | 220KV | 10:47 | 14-09-2020 | 18:03 | 14-09-2020 | For line CT AMP work |
|  | VARSANA - 400KV - Bus 2 | Gujarat | 400KV | 10:30 | 14-09-2020 | 15:13 | 15-09-2020 | Yph and Bph Isolator repairing/maintenance and alignment work at Varsana |
|  | 400KV/220KV CHANDRAPUR-ICT-2 | Maharashtra | 400KV/220KV | 10:19 | 14-09-2020 | 17:18 | 25-09-2020 | For replacement of old fan pump control cubical of R B-ph unit. Replacement of old HCB Isolator with EB one side by new one.For applying the high insulation coating to 33KV IPS tube, PTs and other allied equipments of external delta connection. |
|  | CHAMPA - 765KV - Bus 2 | POWERGRID-WR1 (PGCIL) | 765KV | 10:10 | 14-09-2020 | 21:15 | 14-09-2020 | 765KV B/R-2 AUXILIARY BUS IPS TUBE BPI WORK |
|  | 400KV/220KV Aurangabad-M (Waluj)-ICT-1 | Maharashtra | 400KV/220KV | 09:56 | 14-09-2020 | 21:09 | 18-09-2020 | Testing work |
|  | 220KV-KAWAS-ICHCHAPUR-2 | Gujarat | 220KV | 09:55 | 14-09-2020 | 13:23 | 14-09-2020 | For maintenance work |
|  | 400KV-BABLESHWAR-PADGHE-1 | Maharashtra | 400KV | 09:47 | 14-09-2020 | 18:09 | 14-09-2020 | Chemical cleaning of insulator string |
|  | 220KV-VAPI-VAPI-GUJARAT-1 | Gujarat | 220KV | 09:13 | 14-09-2020 | 18:18 | 14-09-2020 | For maintenance work |
|  | 400KV/220KV Koradi-ICT-2 | Maharashtra | 400KV/220KV | 09:02 | 14-09-2020 | 21:09 | 14-09-2020 | Testing |
|  | 400KV/220KV VARSANA-ICT-2 | Gujarat | 400KV/220KV | 08:19 | 14-09-2020 | 15:32 | 15-09-2020 | To attend 89A gearbox problem |
|  | 400KV-APL-MUNDRA-VARSANA-2 | Gujarat | 400KV | 08:17 | 14-09-2020 | 13:54 | 14-09-2020 | Yph and Bph Isolator repairing/maintenance and alignment work with 400kv Main Bus-02 at Varsana |
|  | 400KV-IEPL-KORADI-II-1 | Maharashtra | 400KV | 08:15 | 14-09-2020 | 20:59 | 14-09-2020 | Line maintenance work. |
|  | 765KV-BINA-GWALIOR-2 | POWERGRID-WR2 (PGCIL) | 765KV | 08:01 | 14-09-2020 | 18:36 | 14-09-2020 | A/R Non Auto / A/R OFF for Tower Strengthening works. |
|  | 765KV-DHARJAYGARH-RANCHI-1 L/R@ DHARAMJAYGARH - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 07:54 | 14-09-2020 | 19:54 | 14-09-2020 | Tamnar Bay Extension Construction Works |
|  | 765KV-DHARAMJAYGARH-RANCHI-1 | POWERGRID-ER,POWERGRID-WR1 (PGCIL) | 765KV | 07:54 | 14-09-2020 | 19:54 | 14-09-2020 | Tamnar Bay Extension Construction Works |
|  | 400KV-SOJA-WANAKBORI-GIS-2 | Gujarat | 400KV | 03:41 | 14-09-2020 | 07:52 | 14-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-SOJA-WANAKBORI-GIS-1 | Gujarat | 400KV | 03:18 | 14-09-2020 | 07:50 | 14-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-TARAPUR 34-PADGHE-1 | POWERGRID-WR2 (PGCIL) | 400KV | 02:22 | 14-09-2020 | 08:51 | 14-09-2020 | Tripped on over voltage / Tripped on over voltage |
|  | 400KV-DEHGAM-WANAKBORI-1 | Gujarat | 400KV | 00:13 | 14-09-2020 | 09:06 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-RANCHODPURA-KANSARI-2 | WTGL-Adani | 400KV | 00:05 | 14-09-2020 | 07:52 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-RANCHODPURA-CHORANIA-2 | WTGL-Adani | 400KV | 00:03 | 14-09-2020 | 07:54 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-KOYNA STAGE IV-LONIKHAND-1 | Maharashtra | 400KV | 23:31 | 13-09-2020 | 08:51 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | GWALIOR - 400KV B/R 3 | POWERGRID-WR2 (PGCIL) | 400KV | 22:53 | 13-09-2020 | 08:07 | 20-09-2020 | On voltage regulation |
|  | GWALIOR - 400KV B/R 2 | POWERGRID-WR2 (PGCIL) | 400KV | 22:52 | 13-09-2020 | 13:19 | 23-09-2020 | On voltage regulation |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 21:46 | 13-09-2020 | 09:13 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-SUGEN-PIRANA-T-2 | Torrent Power (TPL) | 400KV | 20:49 | 13-09-2020 | 07:58 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-AMRELI-HADALA-1 | Gujarat | 400KV | 20:45 | 13-09-2020 | 07:54 | 14-09-2020 | Manually opened due to High Voltage / High voltage |
|  | 400KV-BHUJ-CGPL-1 | POWERGRID-WR2 (PGCIL) | 400KV | 18:55 | 13-09-2020 | 19:30 | 13-09-2020 | B-E fault. A/R Successful at Bhuj end.CGPL end:10.15kA;28.9km. |
|  | 400KV-Bhuj-CGPL-2 | POWERGRID-WR2 (PGCIL) | 400KV | 18:01 | 13-09-2020 | 18:48 | 13-09-2020 | R-E Fault.A/R successful at bhuj tripped at CGPL end |
|  | 400KV-AKOLA (2)-NANDGAONPETH-1 | APTCL,Maharashtra | 400KV | 17:56 | 13-09-2020 | 10:24 | 24-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-SEONI-PG-KHANDWA-2 | POWERGRID-WR1 (PGCIL),POWERGRID-WR2 (PGCIL) | 400KV | 16:49 | 13-09-2020 | 17:08 | 13-09-2020 | Y-E Fault. A/R successful at Khandwa and tripped at Seoni end. |
|  | 400KV-TIRODA-WARORA-2 | ATIL-Adani,Maharashtra | 400KV | 16:19 | 13-09-2020 | 20:12 | 13-09-2020 | Y-E Fault |
|  | 400KV-TIRODA-WARORA-1 | ATIL-Adani,Maharashtra | 400KV | 16:19 | 13-09-2020 | 16:20 | 13-09-2020 | Y-E fault. A/R successful. |
|  | 400KV-TIRODA-WARORA-1 | ATIL-Adani,Maharashtra | 400KV | 15:52 | 13-09-2020 | 15:53 | 13-09-2020 | Y-E Fault.A/R successful |
|  | 765KV/400KV BINA-ICT-2 | POWERGRID-WR2 (PGCIL) | 765KV/400KV | 10:16 | 13-09-2020 | 18:20 | 13-09-2020 | For AMP work. |
|  | 765KV-BINA-JABALPUR-3 | JTCL-Sterlite | 765KV | 09:52 | 13-09-2020 | 18:20 | 13-09-2020 | A/R Non Auto / A/R In non-Auto Mode for Earth wire / OPGW Rectification work |
|  | 765KV-BINA-GWALIOR-2 | POWERGRID-WR2 (PGCIL) | 765KV | 09:22 | 13-09-2020 | 18:53 | 13-09-2020 | A/R Non Auto / A/R OFF for Tower Strengthening works. |
|  | 400KV/220KV VARSANA-ICT-1 | Gujarat | 400KV/220KV | 09:14 | 13-09-2020 | 12:57 | 13-09-2020 | Hot point in 89-B Pentograph |
|  | HVDC 500KV BHADRAWATI Pole 1 | POWERGRID-WR1 (PGCIL) | 500KV | 09:10 | 13-09-2020 | 19:12 | 13-09-2020 | For testing and commissioning of VESDA (Very Early Smoke Detection Apparatus) |
|  | 400KV-JP NIGRIE-SATNA-2 | Jaypee Nigire (JNSTPP) | 400KV | 08:17 | 13-09-2020 | 17:39 | 13-09-2020 | Conductor Repair, earthing shunt tightness, Tower structure tightness work |
|  | 765KV-Wardha-AURANGABAD-3 | POWERGRID-WR1 (PGCIL) | 765KV | 02:16 | 13-09-2020 | 08:15 | 22-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 765KV-Wardha-AURANGABAD-3 L/R@ Wardha - 765KV | POWERGRID-WR1 (PGCIL) | 765KV | 02:16 | 13-09-2020 | 02:44 | 13-09-2020 | Voltage Regulation / LR taken as BR |
|  | 400KV-SOJA-WANAKBORI-GIS-1 | Gujarat | 400KV | 01:46 | 13-09-2020 | 11:50 | 13-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-SOJA-WANAKBORI-GIS-2 | Gujarat | 400KV | 01:45 | 13-09-2020 | 11:51 | 13-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-RANCHODPURA-KANSARI-1 | WTGL-Adani | 400KV | 01:28 | 13-09-2020 | 08:01 | 13-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 400KV-RANCHODPURA-CHORANIA-1 | WTGL-Adani | 400KV | 01:26 | 13-09-2020 | 11:50 | 13-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 400KV-AMRELI-HADALA-1 | Gujarat | 400KV | 01:24 | 13-09-2020 | 11:53 | 13-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 400KV-CHANDRAPUR-KHAPARKHEDA-1 | Maharashtra | 400KV | 01:13 | 13-09-2020 | 08:50 | 13-09-2020 | Tripped on O/v at Chandrapur |
|  | 220KV-BACHAU-Charadvada-1 | Gujarat | 220KV | 00:34 | 13-09-2020 | 01:09 | 13-09-2020 | In Bachhau end R phase to earth fault,fault current-5.15 Kamp,dist-86.5Km.Autoreclose in Charadvada end. |
|  | 220KV-BETUL-SARNI-1 | Madhya Pradesh | 220KV | 23:51 | 12-09-2020 | 23:57 | 12-09-2020 | In Betul end Y phase to earth fault ,Fault current-5.5Kamp,Dist-21.1 Km. Autoreclosed in Sami end. |
|  | GWALIOR - 765KV B/R 1 | POWERGRID-WR2 (PGCIL) | 765KV | 22:44 | 12-09-2020 | 04:26 | 13-09-2020 | Voltage Regulation / VR. |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 21:16 | 12-09-2020 | 09:04 | 13-09-2020 | Manually opened due to High Voltage / MOHV |
|  | MORENA - 400KV B/R 1 | CWRTL-Adani | 400KV | 20:25 | 12-09-2020 | 08:05 | 20-09-2020 | Voltage Regulation / VR |
|  | GWALIOR - 400KV B/R 1 | POWERGRID-WR2 (PGCIL) | 400KV | 20:24 | 12-09-2020 | 13:15 | 23-09-2020 | Voltage Regulation / VR |
|  | 400KV-TIRODA-WARORA-2 | ATIL-Adani,Maharashtra | 400KV | 19:05 | 12-09-2020 | 23:04 | 12-09-2020 | A/T on R-Y phase fault F/C: Ir=3.07kA and Iy=2.3kA and F/D: 199km from Tiroda end, and 12.9kA in each phase and 21.8km from Warora end. |
|  | 400KV-IEPL-WARORA-1 | Maharashtra | 400KV | 18:30 | 12-09-2020 | 21:14 | 12-09-2020 | O/V in Y-phase operated at Warora/ suspected maloperation; taken into service after checking the relay |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 18:18 | 12-09-2020 | 08:25 | 13-09-2020 | Manually opened due to High Voltage / MOHV |
|  | HVDC 500KV VINDHYACHAL Pole 1 | POWERGRID-WR2 (PGCIL) | 500KV | 16:43 | 12-09-2020 | 22:16 | 12-09-2020 | For replacement of faulty thyristors and snubber circuit components. |
|  | 400KV-KHARGHAR-PUNE-PG-1 | Maharashtra,WTPL-Adani | 400KV | 16:30 | 12-09-2020 | 20:32 | 12-09-2020 | To attend Major hotspot on R-ph W.T. upper jumper clamp |
|  | PITHAMPUR - 400KV - Bus 1 | Madhya Pradesh | 400KV | 15:12 | 12-09-2020 | 09:54 | 13-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 220KV-TARAPUR 12-BORIVALI-1 | Maharashtra | 220KV | 14:05 | 12-09-2020 | 19:35 | 12-09-2020 | FIXING OF MISSING SPACERS |
|  | 220KV-TARAPUR 12-BORIVALI-1 | Maharashtra | 220KV | 14:05 | 12-09-2020 | 19:34 | 12-09-2020 | FIXING OF MISSING SPACERS |
|  | GWALIOR - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 13:33 | 12-09-2020 | 19:34 | 12-09-2020 | For attending hot spot on 415 89A isolator. |
|  | EKTUNI - 400KV - Bus 1 | Maharashtra | 400KV | 12:39 | 12-09-2020 | 18:10 | 12-09-2020 | Diagnostic Testing Routine Maintainence |
|  | 400KV/220KV JETPUR-ICT-3 | Gujarat | 400KV/220KV | 12:20 | 12-09-2020 | 16:50 | 12-09-2020 | Hot spots |
|  | 400KV-SSP-RAJGARH-1 | Gujarat,Madhya Pradesh,NCA,POWERGRID-WR2 (PGCIL),SSP (SSNL) | 400KV | 12:13 | 12-09-2020 | 20:06 | 12-09-2020 | A/T on B-phase E/F 2.09KA, 135KM from Rajgarh end. B-phase, Z-1, 5.8KA, 41.4KM from SSP end |
|  | 220KV-TARAPUR 12-BHILAD-1 | Gujarat | 220KV | 11:32 | 12-09-2020 | 14:16 | 12-09-2020 | A/T on B phase to E/F zone-1, F/C: 3.76kA and F/D: 9.26km from Bhilad end. |
|  | 400KV/220KV BHILAI-ICT-1 | Chattisgarh | 400KV/220KV | 11:18 | 12-09-2020 | 14:55 | 12-09-2020 | To attend red hot and heavy sparking in Y phase Isolator current collector assembly. |
|  | PITHAMPUR - 400KV - Bus 2 | Madhya Pradesh | 400KV | 11:02 | 12-09-2020 | 14:40 | 12-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 765KV-DHULE-KHANDWA-1 L/R@ KHANDWA - 765KV | KTL-Sterlite | 765KV | 10:51 | 12-09-2020 | Still out | Still out | Voltage Regulation / VR |
|  | 220KV-KAWAS-HALDARWA-2 | Gujarat | 220KV | 10:42 | 12-09-2020 | 14:28 | 12-09-2020 | To attend burnt jumper cone at location number 263. |
|  | 400KV/220KV PITHAMPUR-ICT-1 | Madhya Pradesh | 400KV/220KV | 10:10 | 12-09-2020 | 18:50 | 12-09-2020 | for s/d on 400kv main bus 1 2 and auxiliary bus at 400kv s/s Pithampur |
|  | 400KV-BINA-MP-JP-BINA-1 | Madhya Pradesh | 400KV | 10:07 | 12-09-2020 | 20:25 | 12-09-2020 | For replacement of damaged sleeves in 400 kV MPPTCL-JP line. |
|  | Main Bay - 765KV-Vindhyachal(PS)-JABALPUR-2 AND Vindhyachal(PS) - 765KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 765KV | 09:49 | 12-09-2020 | 17:21 | 14-09-2020 | Outage availed for AMP, but outage extended due to mechanical problem in spring charging circuit assembly of the Y-PH (MASTER) Breaker |
|  | 765KV-BINA-INDORE-1 | POWERGRID-WR2 (PGCIL) | 765KV | 09:43 | 12-09-2020 | 19:52 | 12-09-2020 | For replacement of damaged sleeves in 400 kV MPPTCL-JP line (At crossing of the line). |
|  | BILASPUR - 765KV - Bus 1 | POWERGRID-WR1 (PGCIL) | 765KV | 09:43 | 12-09-2020 | 20:23 | 12-09-2020 | For AMP works |
|  | 400KV-VELODA-CHARANKA-2 | Gujarat | 400KV | 09:20 | 12-09-2020 | 16:10 | 12-09-2020 | FOR BAY MAINTENANCE WORK |
|  | 765KV-BINA-GWALIOR-2 | POWERGRID-WR2 (PGCIL) | 765KV | 09:00 | 12-09-2020 | 18:27 | 12-09-2020 | A/R Non Auto / A/R OFF for Tower Strengthening works. Proposed by AM TL. |
|  | 400KV/220KV JETPUR-ICT-1 | Gujarat | 400KV/220KV | 09:00 | 12-09-2020 | 12:10 | 12-09-2020 | Hot spots |
|  | 220KV-TARAPUR 12-VAPI-1 | Gujarat | 220KV | 08:32 | 12-09-2020 | 12:35 | 12-09-2020 | A/T on B phase to E/F, Zone-1, FL-60.32 KM , FC:- B ph - 2.254 KA from Tarapur end. |
|  | 765KV-DHARAMJAYGARH-RANCHI-1 | POWERGRID-ER,POWERGRID-WR1 (PGCIL) | 765KV | 08:25 | 12-09-2020 | 19:55 | 12-09-2020 | For Tower Strengthning work , TOTAL - 166 TOWERS, COMPLETED - NIL |
|  | 400KV-Damoh-BIRSINGPUR-1 | POWERGRID-WR2 (PGCIL) | 400KV | 05:33 | 12-09-2020 | 06:03 | 12-09-2020 | Line tripped on Y ph fault. From Damoh end:2.3 kA, 157 km. From Birsingpur-80 km, 4.1 kA |
|  | 132KV-VSTPS-WAIDHAN-1 | Madhya Pradesh,NTPC | 132KV | 03:04 | 12-09-2020 | 03:23 | 12-09-2020 | Line tripped on Y-phase to earth fault zone-1.Fault current-984 amp,Dist-34.13 Km from Waidhan end. |
|  | 400KV-Kolhapur GIS-MAPUSA-2 | POWERGRID-WR1 (PGCIL) | 400KV | 01:54 | 12-09-2020 | 15:48 | 12-09-2020 | Line tripped on B-phase to Earth fault.Fault detail: FD-35.89km, FC-3.046kA from Mapusa end. FD-119.2km, FC-3.32 kA from Kolhapur end. / Trial charge attempted at 02:59hrs, but tripped on SOTF. |
|  | HVDC 500KV APL Pole 2 | ATIL-Adani | 500KV | 01:11 | 12-09-2020 | 08:30 | 12-09-2020 | OLTC protection operation at Mohindergarh. |
|  | 400KV-KHANDWA-DHULE-MS-1 | POWERGRID-WR2 (PGCIL) | 400KV | 01:05 | 12-09-2020 | 17:40 | 23-09-2020 | To control line loading of SSP-Asoj |
|  | 765KV-Pune-GIS-PADGHE-PG-1 | CWRTL-Adani,POWERGRID-WR1 (PGCIL) | 765KV | 00:41 | 12-09-2020 | 08:06 | 19-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 765KV-VADODARA-DHULE-1 | BDTCL-Sterlite | 765KV | 00:10 | 12-09-2020 | 06:23 | 12-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 765KV-VADODARA-DHULE-1 L/R@ DHULE - 765KV | BDTCL-Sterlite | 765KV | 00:10 | 12-09-2020 | 00:14 | 12-09-2020 | Voltage Regulation / VR. |
|  | 765KV-Solapur-PARLI NEW-1 | PPTL-POWERGRID | 765KV | 00:01 | 12-09-2020 | 07:03 | 16-09-2020 | Manually opened due to High Voltage / Manually open on HV. |
|  | 400KV-RAJGARH-KASOR-2 FSC@ RAJGARH | POWERGRID-WR2 (PGCIL) | 400KV | 23:50 | 11-09-2020 | 11:08 | 14-09-2020 | Voltage Regulation / VR. |
|  | 400KV-RAJGARH-KASOR-1 FSC@ RAJGARH | POWERGRID-WR2 (PGCIL) | 400KV | 23:49 | 11-09-2020 | 11:07 | 14-09-2020 | Voltage Regulation / VR. |
|  | 400KV-SEONI-PG-KHANDWA-2 FSC@ KHANDWA | POWERGRID-WR2 (PGCIL) | 400KV | 23:47 | 11-09-2020 | Still out | Still out | Voltage Regulation / VR. |
|  | 400KV-KOYNA STAGE IV-LONIKHAND-1 | Maharashtra | 400KV | 23:43 | 11-09-2020 | 08:29 | 12-09-2020 | MOHV |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 22:12 | 11-09-2020 | 08:48 | 12-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KARAD-JAIGAD-2 | Maharashtra | 400KV | 21:03 | 11-09-2020 | 08:10 | 15-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-RGPPL-NAGOTHANE-2 | Maharashtra | 400KV | 20:55 | 11-09-2020 | 10:31 | 12-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-KASOR-CHORANIA-1 | Gujarat | 400KV | 19:08 | 11-09-2020 | 07:55 | 12-09-2020 | R-phase fault; 70.5km,4.18kA@Kasor;16km,12.57kA@Chorania |
|  | 400KV-SOJA-WANAKBORI-GIS-1 | Gujarat | 400KV | 17:45 | 11-09-2020 | 17:12 | 12-09-2020 | Line tripped on R-E fault. From Wanakbori end-6.04 kA, 75 km |
|  | 400KV-DHULE-MS-BABLESHWAR-1 | Maharashtra | 400KV | 17:43 | 11-09-2020 | 08:15 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 16:03 | 11-09-2020 | 11:26 | 12-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV/220KV PADGHE-ICT-3 | Maharashtra | 400KV/220KV | 14:42 | 11-09-2020 | 19:56 | 11-09-2020 | Attending hotspots and connecting cable of PRD relay |
|  | 400KV-APL-MUNDRA-SAMI-1 FSC@ SAMI | ATIL-Adani | 400KV | 14:37 | 11-09-2020 | 17:13 | 11-09-2020 | to facilitate E/S/D of APL Mundra-Sami-1 for attending hot spot on jumper cone of tower no 44 and 159. |
|  | 400KV-APL-MUNDRA-SAMI-1 | ATIL-Adani | 400KV | 14:37 | 11-09-2020 | 17:13 | 11-09-2020 | For attending hot spot on jumper cone of tower no 44 and 159. |
|  | 400KV/220KV VARSANA-ICT-4 | Gujarat | 400KV/220KV | 14:20 | 11-09-2020 | 16:55 | 11-09-2020 | B-phase pentograph isolator Hotspot |
|  | 220KV-PARLI-PARLI-M-1 | Maharashtra | 220KV | 12:49 | 11-09-2020 | 17:14 | 11-09-2020 | Tightening of nut bolt and fixing nut bolts to cross arms supporting pieces of line towers of newly commissioned LILO section of PGCIL ckt |
|  | 400KV-TAPTHITHANDA-EKTUNI-1 | Maharashtra | 400KV | 11:46 | 11-09-2020 | 17:46 | 11-09-2020 | To attend the hotspot of 408, 89B isolator. |
|  | 400KV/220KV BABLESHWAR-ICT-1 | Maharashtra | 400KV/220KV | 11:37 | 11-09-2020 | 20:02 | 12-09-2020 | Diagnostic testing |
|  | 400KV-BHADRAWATI-PARLI-1 | POWERGRID-WR1 (PGCIL) | 400KV | 11:28 | 11-09-2020 | 20:40 | 11-09-2020 | Shutdown of line for crossing OPGW overhead 400kV BHADRAVATI-DHARIWAL TPP II AR to be kept in Non-auto mode for safety of precautions. |
|  | DHARAMJAYGARH - 400KV - Bus 2 | POWERGRID-WR1 (PGCIL) | 400KV | 11:17 | 11-09-2020 | 18:35 | 11-09-2020 | For AMP works// |
|  | 400KV-Koradi-SATPURA-1 | POWERGRID-WR1 (PGCIL) | 400KV | 11:16 | 11-09-2020 | 06:19 | 12-09-2020 | For AMP works |
|  | NAVSARI - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 11:14 | 11-09-2020 | 17:43 | 11-09-2020 | AMP works at Navsari GIS SS |
|  | AURANGABAD - 765KV - Bus 1 | POWERGRID-WR1 (PGCIL) | 765KV | 11:10 | 11-09-2020 | 20:10 | 11-09-2020 | For AMP works// |
|  | 220KV-Malanpur-Auriya-1 | Madhya Pradesh | 220KV | 10:38 | 11-09-2020 | 18:58 | 11-09-2020 | For line maintenance work// |
|  | Damoh - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 10:34 | 11-09-2020 | 19:27 | 11-09-2020 | For attending zero current through Y phase of main bay 413 (bus side isolator). |
|  | KHANDWA-PS - 400KV B/R 1 | KTL-Sterlite | 400KV | 10:33 | 11-09-2020 | 18:58 | 11-09-2020 | AMP works + PSD/CSD comissioning// |
|  | 400KV-BINA-SHUJALPUR-2 | POWERGRID-WR2 (PGCIL) | 400KV | 10:15 | 11-09-2020 | 19:40 | 11-09-2020 | AMP WORK LINE TERMINAL EQUIPMEMNT at Shujalpur. Line AMP works on opportunity. A/R OFF of ckt-1 and dia to be kept open at both ends. |
|  | 400KV-BHADRAWATI-DHARIWAL-1 | Dhariwal-STU (DIL),POWERGRID-WR1 (PGCIL) | 400KV | 10:09 | 11-09-2020 | 19:08 | 11-09-2020 | Shutdown of line for crossing OPGW overhead |
|  | SASAN - 765KV - Bus 2 | SASAN\_UMPP (SPL) | 765KV | 10:01 | 11-09-2020 | 22:30 | 11-09-2020 | ANNUAL MAINTENANCE //SASAN - 765KV - BUS 2A |
|  | 400KV-BHILAI-RAITA-2 | Chattisgarh | 400KV | 09:59 | 11-09-2020 | 18:37 | 11-09-2020 | Scheduled Maint. Testing work of Reactor,Breaker,CT, Isolator,LA, CVT WT.// |
|  | 400KV-RGPPL-NAGOTHANE-2 | Maharashtra | 400KV | 09:30 | 11-09-2020 | 20:54 | 11-09-2020 | Routine Maintenance work |
|  | HVDC 800KV Raigarh-GIS-HVDC Pole 1 | POWERGRID-WR1 (PGCIL) | 800KV | 09:22 | 11-09-2020 | 13:14 | 11-09-2020 | A/T due to DC line voltage measurement faulty. |
|  | 400KV/220KV BHOPAL-MP-ICT-1 | Madhya Pradesh | 400KV/220KV | 09:15 | 11-09-2020 | 16:49 | 11-09-2020 | Post monsoon maintenance work. |
|  | 765KV-DHARAMJAYGARH-RANCHI-1 | POWERGRID-ER,POWERGRID-WR1 (PGCIL) | 765KV | 09:12 | 11-09-2020 | 19:42 | 11-09-2020 | For Tower Strengthning work , TOTAL - 166 TOWERS, COMPLETED - NIL |
|  | 400KV-UKAI-KOSAMBA-2 | Gujarat | 400KV | 09:07 | 11-09-2020 | 19:00 | 11-09-2020 | For tree cutting work between loc no.168-169. A/R of 400 KV Kosamba-Vav line will remain out. |
|  | 765KV-BINA-GWALIOR-2 | POWERGRID-WR2 (PGCIL) | 765KV | 09:04 | 11-09-2020 | 19:21 | 11-09-2020 | A/R Non Auto / A/R OFF for Tower Strengthening works. Proposed by AM TL |
|  | 400KV-RANCHODPURA-KANSARI-1 | WTGL-Adani | 400KV | 08:46 | 11-09-2020 | 19:01 | 11-09-2020 | For bay PMM work and Veloda-Kansari Ar off for WTGL |
|  | 400KV-BHADRAWATI-GWEL-1 | GMR WARORA (GWEL) | 400KV | 08:32 | 11-09-2020 | 18:16 | 11-09-2020 | Shut down for OPGW work between tower 90-91 along with outage of line crossings(Bhadrawati – Dhariwal Bhadrawati – Parli on 8th Sep 2020 ) |
|  | 400KV-CGPL-JETPUR-1 | POWERGRID-WR2 (PGCIL) | 400KV | 08:17 | 11-09-2020 | 12:05 | 13-09-2020 | New SPS relay installation,Isolator maintenance,Equipments testing terminal tightness |
|  | 400KV/220KV BOISAR-ICT-1 | POWERGRID-WR2 (PGCIL) | 400KV/220KV | 07:12 | 11-09-2020 | 11:55 | 11-09-2020 | Hot spot in 201-89-C-R-Ph isolator |
|  | 400KV-KALWA-PADGHE-1 | Maharashtra | 400KV | 23:45 | 10-09-2020 | 08:32 | 11-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-DHULE-MS-BABLESHWAR-2 | Maharashtra | 400KV | 20:00 | 10-09-2020 | 08:42 | 11-09-2020 | Manually opened due to High Voltage / manually opened on HV |
|  | 220KV-KHANDWA-CHHEGAON-1 | Madhya Pradesh | 220KV | 18:44 | 10-09-2020 | 19:34 | 10-09-2020 | B\_N / Khandwa- B\_N,Z\_2,55km,2.7kA Chegaon- B\_N,Z\_1,0.65km,3.6KA |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 18:07 | 10-09-2020 | 08:04 | 11-09-2020 | Manually opened on high voltage |
|  | PITHAMPUR - 400KV - Bus 2 | Madhya Pradesh | 400KV | 17:40 | 10-09-2020 | 20:01 | 10-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 400KV-KORBA WEST EXTENSION-MARWA-1 | Chattisgarh | 400KV | 17:25 | 10-09-2020 | 10:40 | 11-09-2020 | Tripped on B-E fault / Zone-1, 7.3 km and 10 kA from Marwa end |
|  | 220KV-MAHALAXMI(KONALKATTA)-AMONA-1 | GOA (GED),Maharashtra | 220KV | 16:21 | 10-09-2020 | 16:43 | 10-09-2020 | Tripped simultaneously during failure of HV side LA of 100MVA ICT-1 at Ponda SS |
|  | 220KV-SATNA-MAIHAR-1 | Madhya Pradesh | 220KV | 15:56 | 10-09-2020 | 16:35 | 10-09-2020 | Tripped on B-E fault / Zone-1, 21.6 km, 2.9 kA from Maihar end, 10.7 km, 9.5 kA from Satna end |
|  | 220KV-KAWAS-HALDARWA-2 | Gujarat | 220KV | 14:26 | 10-09-2020 | 15:56 | 10-09-2020 | Replacement of faulty trip coil in Rph of CB and clearing DC fault in the same |
|  | PITHAMPUR - 400KV - Bus 1 | Madhya Pradesh | 400KV | 13:30 | 10-09-2020 | 16:59 | 10-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | Bhuj - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 13:07 | 10-09-2020 | 20:36 | 10-09-2020 | For attending hot spot in 40789A Rph bus side isolator |
|  | 400KV-INDIRASAGAR-INDORE-MP-1 | Madhya Pradesh | 400KV | 12:58 | 10-09-2020 | 13:14 | 10-09-2020 | Tripped on R-E fault / zone-2, 94.42 km, 2.5 kA from Indore end. A/R successful from Indirasagar end |
|  | 400KV-Pune-GIS-PARLI-1 | POWERGRID-WR1 (PGCIL),WTPL-Adani | 400KV | 12:55 | 10-09-2020 | 19:18 | 10-09-2020 | For attending hot spot on line Isolators |
|  | SATNA - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 12:50 | 10-09-2020 | 18:34 | 10-09-2020 | To replace support stack and melted contact of 40189A, Rph bus side insulator |
|  | 400KV-Badnawar-PITHAMPUR-2 | Madhya Pradesh | 400KV | 12:19 | 10-09-2020 | 20:50 | 12-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 400KV-Badnawar-PITHAMPUR-1 | Madhya Pradesh | 400KV | 12:10 | 10-09-2020 | 20:05 | 12-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 400KV-SINGAJI-PITHAMPUR-4 | Madhya Pradesh | 400KV | 12:00 | 10-09-2020 | 20:20 | 12-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 400KV-BHILAI-Koradi-1 | POWERGRID-WR1 (PGCIL) | 400KV | 11:35 | 10-09-2020 | 21:01 | 10-09-2020 | For AMP works |
|  | 765KV-DHARAMJAYGARH-JABALPUR-4 | JTCL-Sterlite | 765KV | 11:24 | 10-09-2020 | 19:11 | 10-09-2020 | A/R Non Auto / for Earthwire / OPGW Rectification work |
|  | 400KV-SINGAJI-PITHAMPUR-3 | Madhya Pradesh | 400KV | 11:13 | 10-09-2020 | 19:44 | 12-09-2020 | For overhead Gantry to Gantry stringing work for additional 315 MVA ICT bay, alignment of isolators and erection of IPS tube at 400kv s/s Pithampur |
|  | 220KV-SATNA-CHHATTARPUR-1 | Madhya Pradesh | 220KV | 11:07 | 10-09-2020 | 12:14 | 10-09-2020 | Tripped on B-E fault / Zone-1, 66.5 km 1.9.kA from Satna end, 78.2 km, 1.09 kA from Chhatarpur end |
|  | 220KV-PARLI-PARLI-M-1 | Maharashtra | 220KV | 11:00 | 10-09-2020 | 17:25 | 10-09-2020 | Tightening of nut bolt and fixing nut bolts to cross arms supporting pieces of line towers of newly commissioned LILO section of PGCIL ckt |
|  | 400KV/220KV Aurangabad-M (Waluj)-ICT-2 | Maharashtra | 400KV/220KV | 10:23 | 10-09-2020 | 19:24 | 10-09-2020 | For dismantling old fire protection scheme diagnostic testing |
|  | DEHGAM - 400KV - Bus 1 | POWERGRID-WR2 (PGCIL) | 400KV | 10:18 | 10-09-2020 | 14:08 | 10-09-2020 | For rectification of broken Rigid BPI connector of R-ph BPI |
|  | 400KV/220KV SOLAPUR-M-ICT-2 | Maharashtra | 400KV/220KV | 10:17 | 10-09-2020 | 18:54 | 10-09-2020 | RTV coating work fire fighting testing |
|  | 765KV/400KV BINA-ICT-1 | POWERGRID-WR2 (PGCIL) | 765KV/400KV | 10:09 | 10-09-2020 | 19:00 | 10-09-2020 | For AMP Work |
|  | SASAN - 765KV - Bus 4 | SASAN\_UMPP (SPL) | 765KV | 10:03 | 10-09-2020 | 23:29 | 10-09-2020 | Annual maintenance |
|  | 400KV/220KV BHOPAL-MP-ICT-1 | Madhya Pradesh | 400KV/220KV | 09:58 | 10-09-2020 | 19:30 | 10-09-2020 | Maintenance work |
|  | 400KV-SIPAT-RANCHI-2 | POWERGRID-WR1 (PGCIL) | 400KV | 09:38 | 10-09-2020 | 19:59 | 10-09-2020 | For Flashed Insulator Replacement in Tower No. 1097 and 811 |
|  | CHAKAN - 400KV - Bus 2 | Maharashtra | 400KV | 09:34 | 10-09-2020 | 18:55 | 10-09-2020 | For replacement of Main bus 2 B-ph isolator Scissor. |
|  | 400KV-KORBA-NTPC-BIRSINGPUR-1 | POWERGRID-WR1 (PGCIL) | 400KV | 09:28 | 10-09-2020 | 19:36 | 10-09-2020 | For Bay Preventive Maintenance at NTPC Korba end, |
|  | KOLHAPUR-MS - 400KV B/R 1 | POWERGRID-WR1 (PGCIL) | 400KV | 09:27 | 10-09-2020 | 17:07 | 10-09-2020 | On voltage regulation |
|  | 400KV/220KV PARLI-M-ICT-3 | Maharashtra | 400KV/220KV | 09:18 | 10-09-2020 | 18:58 | 10-09-2020 | CT Circuit Breaker testing work |
|  | 400KV-APL-MUNDRA-HADALA-1 | Gujarat | 400KV | 08:30 | 10-09-2020 | 15:49 | 10-09-2020 | For PG Isolator maintanance work and feeder bay maint work |
|  | 400KV-KARAD-NEW KOYNA-2 | Maharashtra | 400KV | 07:59 | 10-09-2020 | 08:27 | 11-09-2020 | For insulator replacement work |
|  | 400KV-KARAD-NEW KOYNA-1 | Madhya Pradesh | 400KV | 07:59 | 10-09-2020 | Still out | Still out | For insulator replacement work |
|  | 400KV-BHUSAWAL-BABLESHWAR-1 | Maharashtra | 400KV | 07:18 | 10-09-2020 | 17:03 | 10-09-2020 | Replacement of faulty Insulator strings |
|  | 400KV-KALWA-PADGHE-2 | Maharashtra | 400KV | 02:05 | 10-09-2020 | 09:02 | 10-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV/220KV JABALPUR-ICT-2 | POWERGRID-WR2 (PGCIL) | 400KV/220KV | 01:15 | 10-09-2020 | 02:30 | 10-09-2020 | B ph PT 2 Failed.Bus Bar Protection operated |
|  | 220KV-JABALPUR-MP-JABALPUR-2 | Madhya Pradesh | 220KV | 01:14 | 10-09-2020 | 02:32 | 10-09-2020 | B ph PT Failed at Jabalpur.Bus Bar Protection operated |
|  | JABALPUR - 220KV - Bus 2 | POWERGRID-WR2 (PGCIL) | 220KV | 01:14 | 10-09-2020 | 02:22 | 10-09-2020 | B ph PT failed.Bus Bar Protection operated. / Bus charged after isolating the faulty B-phPT. |
|  | 765KV-AURANGABAD-Solapur-2 | POWERGRID-WR1 (PGCIL) | 765KV | 21:34 | 09-09-2020 | 08:53 | 15-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-AKOLA (2)-NANDGAONPETH-1 | APTCL,Maharashtra | 400KV | 17:08 | 09-09-2020 | 08:34 | 13-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-DHULE-MS-BABLESHWAR-2 | Maharashtra | 400KV | 16:33 | 09-09-2020 | 07:07 | 10-09-2020 | Manually opened due to High Voltage / HV |
|  | 765KV-DHARAMJAYGARH-JABALPUR-4 | JTCL-Sterlite | 765KV | 11:51 | 09-09-2020 | 18:19 | 10-09-2020 | A/R Non Auto / for Earthwire / OPGW Rectification work |
|  | 765KV-Pune-GIS-Solapur-1 | POWERGRID-WR1 (PGCIL) | 765KV | 11:39 | 09-09-2020 | 11:15 | 14-09-2020 | Manually opened due to High Voltage / Voltage regulation as per system requirement |
|  | 400KV/220KV BINA-MP-ICT-2 | Madhya Pradesh | 400KV/220KV | 11:35 | 09-09-2020 | 20:29 | 12-09-2020 | To attend problem in isolator |
|  | HVDC 500KV BHADRAWATI Pole 2 | POWERGRID-WR1 (PGCIL) | 500KV | 10:55 | 09-09-2020 | 03:38 | 10-09-2020 | For AMP works/HVDC/ |
|  | 400KV-BHUSAWAL-Aurangabad-M (Waluj)-1 | Maharashtra | 400KV | 17:09 | 08-09-2020 | 06:54 | 10-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV/220KV DGEN-ICT-3 | DGEN | 400KV/220KV | 16:34 | 08-09-2020 | Still out | Still out | ICT routine energisation testing during RSD and shutdown for energy conservation after one day energization. |
|  | GWALIOR - 400KV B/R 3 | POWERGRID-WR2 (PGCIL) | 400KV | 15:05 | 08-09-2020 | 06:13 | 13-09-2020 | Voltage Regulation / VR. |
|  | 400KV-DHULE-MS-BABLESHWAR-1 | Maharashtra | 400KV | 14:42 | 08-09-2020 | 07:04 | 10-09-2020 | Tripped on R-E fault.Dhule: 92 km, 4.08 kA |
|  | 400KV/220KV DGEN-ICT-2 | DGEN | 400KV/220KV | 14:41 | 08-09-2020 | Still out | Still out | ICT routine energisation testing during RSD and shutdown for energy conservation after one day energization. |
|  | 400KV-SEONI-PG-KHANDWA-1 FSC@ KHANDWA | POWERGRID-WR2 (PGCIL) | 400KV | 11:42 | 08-09-2020 | Still out | Still out | while taking into service due to the Force Trigger Path fail in both the systems at a time. |
|  | GWALIOR - 400KV B/R 2 | POWERGRID-WR2 (PGCIL) | 400KV | 11:20 | 08-09-2020 | 06:14 | 13-09-2020 | Voltage Regulation / VR |
|  | INDORE - 765KV B/R 2 | POWERGRID-WR2 (PGCIL) | 765KV | 10:30 | 08-09-2020 | 09:24 | 15-09-2020 | Voltage Regulation / VR |
|  | 400KV/220KV DGEN-ICT-1 | DGEN | 400KV/220KV | 10:26 | 08-09-2020 | Still out | Still out | ICT routine energisation testing during RSD and shutdown for energy conservation after one day energization . |
|  | 400KV/22KV DGEN-GT-1 | DGEN | 400KV/22KV | 10:26 | 08-09-2020 | Still out | Still out | ICT routine energisation testing during RSD and shutdown for energy conservation after one day energization |
|  | 400KV/220KV DGEN-ICT-1 | DGEN | 400KV/220KV | 10:26 | 08-09-2020 | Still out | Still out | ICT routine energisation testing during RSD and shutdown for energy conservation after one day energization |
|  | INDORE - 765KV B/R 1 | POWERGRID-WR2 (PGCIL) | 765KV | 19:43 | 07-09-2020 | 00:13 | 12-09-2020 | Voltage Regulation / VR |
|  | 400KV-Kirnapur-BHILAI-1 | Chattisgarh,Madhya Pradesh | 400KV | 17:50 | 07-09-2020 | Still out | Still out | Manually opened due to High Voltage / MOHV |
|  | 400KV-DHULE-MS-BABLESHWAR-1 | ACPL | 400KV | 21:05 | 06-09-2020 | Still out | Still out | Manually opened on High Voltaage / MOHV |
|  | 400KV-AMARAVATI-AKOLA-1 | Madhya Pradesh | 400KV | 20:57 | 06-09-2020 | Still out | Still out | Manually opened due to High Voltage / HV |
|  | 400KV/220KV KANSARI-ICT-1 | Gujarat | 400KV/220KV | 09:35 | 06-09-2020 | Still out | Still out | Peacock electrocuted on tertiary; LA damaged |
|  | 400KV-BINA-BINA-NHPTL-1 | NHPTL,POWERGRID-WR2 (PGCIL) | 400KV | 01:20 | 04-09-2020 | Still out | Still out | Testing complete. |
|  | 400KV/22KV DGEN-GT-2 | DGEN | 400KV/22KV | 12:43 | 03-09-2020 | 09:40 | 01-10-2020 | Unit 52 De-energization of Transformer for Energy Conservation during RSD. Transformer will remain de-energized and available |
|  | 765KV-RAIPUR-PS (DURG)-JHARSUGUDA-1 | OGPTL | 765KV | 01:33 | 02-09-2020 | 21:10 | 23-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-VINDHYANCHAL-III-VINDHYACHAL-V-1 | NTPC | 400KV | 19:27 | 31-08-2020 | Still out | Still out | To control fault level at VSTPS |
|  | 400KV-VINDHYANCHAL-III-VINDHYACHAL-V-2 | NTPC | 400KV | 19:27 | 31-08-2020 | Still out | Still out | To control fault level at VSTPS |
|  | 765KV-Pune-GIS-PADGHE-PG-1 | CWRTL-Adani,POWERGRID-WR1 (PGCIL) | 765KV | 18:25 | 31-08-2020 | 10:38 | 11-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV-CHORANIA-KOSAMBA-1 | Gujarat | 400KV | 13:42 | 31-08-2020 | Still out | Still out | Tripped on Y-phase fault.Kosamba end: Z1, Y ph, 29 km, 8.39 kA. Chorania end: Z1, Y ph, 207 km, 2.24 kA, Cross arm damaged |
|  | 400KV-CHARAL-KOSAMBA-1 | Gujarat | 400KV | 13:42 | 31-08-2020 | 19:42 | 29-09-2020 | Tripped on Y-phase fault.Kosamba end:Z1, Y, 8.89 kA, 27.2 km, SOTF. Charal end: Z1, Y, 1.9 kA, 182 km, SOTF. Cross arm damage |
|  | 765KV-Wardha-RAIPUR-PS (DURG)-4 | POWERGRID-WR1 (PGCIL) | 765KV | 19:00 | 29-08-2020 | 12:00 | 25-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 765KV-Wardha-AURANGABAD-1 | POWERGRID-WR1 (PGCIL) | 765KV | 21:52 | 27-08-2020 | 10:11 | 16-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 132KV-PENCH-MP-KANHAN-1 | Madhya Pradesh,Maharashtra | 132KV | 02:37 | 23-08-2020 | Still out | Still out | A/T from Kanhan end due to distance protection operated. |
|  | GWALIOR - 400KV B/R 1 | POWERGRID-WR2 (PGCIL) | 400KV | 19:21 | 22-08-2020 | 06:46 | 12-09-2020 | Voltage Regulation / VR |
|  | MORENA - 400KV B/R 1 | CWRTL-Adani | 400KV | 19:37 | 15-08-2020 | 06:29 | 12-09-2020 | Voltage Regulation / VR |
|  | 765KV-DHARAMJAYGARH-JABALPUR-3 | Madhya Pradesh,Maharashtra | 765KV | 19:41 | 13-08-2020 | Still out | Still out | Manually opened due to High Voltage / Manually opened due to high voltage |
|  | 765KV-DHARAMJAYGARH-JABALPUR-3 | JTCL-Sterlite | 765KV | 19:39 | 13-08-2020 | Still out | Still out | Manually opened due to High Voltage / Taken out on O/V |
|  | 400KV-KORBA WEST-KORBA-NTPC-1 | POWERGRID-WR1 (PGCIL) | 400KV | 09:12 | 11-08-2020 | Still out | Still out | To control the fault level at Korba NTPC |
|  | 400KV/220KV KOLHAPUR-ICT-1 | Maharashtra | 400KV/220KV | 09:58 | 10-08-2020 | Still out | Still out | for replacement of existing 400/220KV 315MVA ICT by 3x167MVA at kolhapur (MS) substation |
|  | 400KV-Raigarh-RAIGARH-PS-1 | POWERGRID-WR1 (PGCIL) | 400KV | 21:19 | 07-08-2020 | Still out | Still out | To control fault level at Kotra; Line idle charged from Raigarh end |
|  | 400KV-Raigarh-RAIGARH-PS-2 | POWERGRID-WR1 (PGCIL) | 400KV | 21:19 | 07-08-2020 | Still out | Still out | To control fault level at Kotra; Line idle charged from Raigarh end |
|  | 132KV-MANSAR-MS-PENCH-1 | Madhya Pradesh,Maharashtra | 132KV | 12:58 | 05-08-2020 | Still out | Still out | Tripped from pench end, IDle chareg from mansar end, |
|  | 765KV-BINA-BINA-NHPTL-1 | NHPTL,POWERGRID-WR2 (PGCIL) | 765KV | 17:33 | 28-07-2020 | Still out | Still out | Testing complete |
|  | HVDC 800KV Raigarh-GIS-HVDC Pole 2 | POWERGRID-WR1 (PGCIL) | 800KV | 16:02 | 20-07-2020 | 09:16 | 16-09-2020 | Blocked after completion of testing. |
|  | HVDC800KV-Raigarh-PUGALUR-2 | POWERGRID-SR,POWERGRID-WR1 (PGCIL) | 800KV | 16:02 | 20-07-2020 | Still out | Still out | blocked after testing |
|  | Tie Bay - 765KV-JABALPUR-BHOPAL-1 AND 765KV/400KV BHOPAL-ICT-2 | BDTCL-Sterlite | 765KV | 08:52 | 16-07-2020 | Still out | Still out | taken out for AMP but outage continued due to Y1 B1 poles of breakers are not operating |
|  | 400KV-BABLESHWAR-IB-NASIK-1 | Maharashtra | 400KV | 11:00 | 11-06-2020 | 10:08 | 11-09-2020 | Manually opened due to High Voltage / MOHV |
|  | 400KV/220KV BHILAI-ICT-3 | Chattisgarh | 400KV/220KV | 21:10 | 28-05-2020 | Still out | Still out | Fire in R phase Bushing. |
|  | 132KV-BINA-MP-MORWA-1 | Madhya Pradesh | 132KV | 19:55 | 27-05-2020 | Still out | Still out | Power not required by Bina(UP) |
|  | 132KV-RAJGHAT-LALITPUR-1 | Madhya Pradesh | 132KV | 18:03 | 19-05-2020 | Still out | Still out | Line hand tripped from Rajghat as requested from UPPTCL. |
|  | NANDGAONPETH - 400KV B/R 1 | Rattan India (RIPL) | 400KV | 21:59 | 29-03-2020 | Still out | Still out | PRV and Buchholz tripped / PRV and Buchholz tripped |
|  | Tie Bay - 765KV-CHAMPA-DHARAMJAYGARH-2 AND 765KV/400KV CHAMPA-ICT-6 | POWERGRID-WR1 (PGCIL) | 765KV | 17:30 | 19-03-2020 | Still out | Still out | SF6 gas leakage from 722 Bay Circuit Breaker Interrupter Housing (R Phase Slave Pole). |
|  | 400KV-SAGAR-SATNA-1 L/R@ SAGAR - 400KV | Madhya Pradesh | 400KV | 01:24 | 04-03-2020 | Still out | Still out | Hand Tripped after testing of first time charging. |
|  | 400KV-Raigarh-RAIPUR-3 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 22:11 | 01-02-2020 | Still out | Still out | Voltage Regulation / VR |
|  | 400KV-Raigarh-RAIPUR-4 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 22:09 | 01-02-2020 | Still out | Still out | Voltage Regulation / VR |
|  | 400KV-VADINAR-BACHAU-2 | POWERGRID-WR2 (PGCIL) | 400KV | 16:00 | 17-12-2019 | Still out | Still out | Manually opened due to High Voltage / MOHV |
|  | 765KV-DHULE-KHANDWA-1 L/R@ DHULE - 765KV | BDTCL-Sterlite | 765KV | 16:42 | 22-10-2019 | Still out | Still out | PRV-1 operated. |
|  | 400KV/132KV VINDHYACHAL-ICT-1 | NTPC | 400KV/132KV | 10:40 | 13-10-2019 | Still out | Still out | due to 200MVA ICT-I got fire bus-3 bus bar protection operated |
|  | 400KV-PARLI-M-LONIKHAND-II-2 L/R@ LONIKHAND-II - 400KV | Maharashtra | 400KV | 18:47 | 02-10-2019 | Still out | Still out | completion of its life and deviation of its parameters |
|  | 400KV-Wardha-WARORA-PG-1 L/R@ Wardha - 400KV | POWERGRID-WR1 (PGCIL) | 400KV | 11:32 | 09-09-2019 | Still out | Still out | For observation purpose |
|  | 132KV-MOUDA-MOUDA-MH-1 | Maharashtra | 132KV | 23:27 | 29-07-2019 | Still out | Still out | For attending Higher Leakage current of LA at Mouda end. |
|  | 400KV/220KV SOJA-ICT-1 | Gujarat | 400KV/220KV | 09:51 | 26-07-2019 | Still out | Still out | dismantling the existing old ICT and erecting new ICT; spares will be used in ICT-2 |
|  | BABLESHWAR - 400KV B/R 2 | Maharashtra | 400KV | 19:12 | 26-06-2019 | Still out | Still out | Failure of Bushing due to which Bus Reactor caught fire |
|  | GMR CHHATTISGARH - 400KV B/R 1 | REL | 400KV | 16:15 | 23-05-2019 | 11:14 | 30-09-2020 | oil leakage |
|  | DHARIWAL - 400KV B/R 1 | Dhariwal-STU (DIL) | 400KV | 08:21 | 12-04-2019 | Still out | Still out | differential PROTECTION OPERATED. |
|  | 400KV-RAIPUR-Wardha-2 FSC@ Wardha | POWERGRID-WR1 (PGCIL) | 400KV | 14:12 | 17-11-2018 | Still out | Still out | Tripped along with the line; line tripped on fault;As intimated by RTAMC During dissipation of surge energy of fault during AR, the Damping resistor, IPS tube connectors to Damping resistor, cables to trigatron circuit of Raipur FSC#2 was damaged. |
|  | 400KV/220KV PADGHE-ICT-1 | Maharashtra | 400KV/220KV | 10:07 | 15-11-2018 | Still out | Still out | Differential protection operated on LV side |
|  | BHUSAWAL - 400KV B/R 1 | Maharashtra | 400KV | 13:49 | 10-11-2018 | Still out | Still out | Caught fire |
|  | 400KV-Wardha-WARORA-PG-2 L/R@ Wardha - 400KV | POWERGRID-WR1 (PGCIL) | 400KV | 08:32 | 04-05-2018 | Still out | Still out | Planned outage taken along with line outage for LILO work of Wardha-Parli D/c at Warora PS, Later not revived along with LILO line 400kV Wardha-Warora PS D/c line. |
|  | 400KV/220KV SATPURA-ICT-1 | Madhya Pradesh | 400KV/220KV | 21:53 | 19-04-2018 | Still out | Still out | differential protection operated |
|  | 400KV-RAIPUR-Wardha-1 FSC@ Wardha | POWERGRID-WR1 (PGCIL) | 400KV | 14:04 | 01-02-2018 | Still out | Still out | A/R Operated successfully at both end; Damping resistor burnt |
|  | PADGHE - 400KV B/R 1 | Maharashtra | 400KV | 00:00 | 13-01-2018 | 16:35 | 25-09-2020 | Bushing tan delta high. |
|  | 400KV-KARAD-Solapur-1 | Maharashtra,WTPL-Adani | 400KV | 09:40 | 15-11-2017 | Still out | Still out | Quarterly Maint At Karad And line maint Work by Lamboti; portions idle charged from both ends, Middle portion used fro 220kV Solapur-Jeur line |
|  | 1200KV/400KV BINA-ICT-2 | POWERGRID-WR2 (PGCIL) | 1200KV/400KV | 06:31 | 12-03-2017 | Still out | Still out | BUCHHHOLTZ OPERATED |
|  | 400KV-CHANDRAPUR-GCR-PARLI-M-3 L/R@ CHANDRAPUR-GCR - 400KV | Maharashtra | 400KV | 00:00 | 21-09-2016 | Still out | Still out | LR Faulty, Under Repairining |
|  | 400KV-Raigarh-RAIPUR-1 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 08:42 | 08-07-2016 | Still out | Still out | main control system computer failure |
|  | 400KV-Raigarh-RAIPUR-2 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 07:48 | 06-07-2016 | Still out | Still out | DUE TO FIRE AT TCSC |
|  | 400KV-ATHENA-Raigarh-2 | ACPL | 400KV | 11:46 | 01-05-2016 | Still out | Still out | FOR TESTING AND CHECKING WORKS/ Kept out after FTC |
|  | 400KV-ATHENA-Raigarh-1 | ACPL | 400KV | 22:02 | 30-04-2016 | Still out | Still out | Y-PH df/dt relay operatec at Athena; provision of df/dt relay at Athena and settings are being checked by Athena/ Kept out after FTC |
|  | 400KV-MANSAR-CHORANIA-1 L/R@ CHORANIA - 400KV | Gujarat | 400KV | 08:34 | 20-01-2015 | Still out | Still out | Availed along with line to carry out LILO works at Mansar by GETCO, Line LILOed at Mansar Mansar - Limbdi charged at 18:01hrs/24.01.15 Hrs Mansar - Mundra charged at 19:17Hrs/24.01.15. but LR not revived at Limbdi |

D. परागमन का प्रतिबंध (यदि कोई हो) Transmission Constraints IEGC 5.5.1.C (D) (IF ANY) : Annexure-I

E. Instances of Persistent / Significant Non-Compliance of IEGC 5.5.1.C (E) : Annexure-II

F. Instances of Congestion In Transmission System IEGC 5.5.1.C (F) (IF ANY) : Annexure-III -NIL

G.कोणीय विभाजन उल्लंघन की रिपोर्टAngular separation violation **:** Annexure-IV

H**.** साप्ताहिक विद्युत दाब विचलन सूचकांकWeekly VDI From **:** Annexure-V

**I. Instances of Inordinate delays in restoration of Transmission elements and Generating units: -**

|  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| **अनु क्रमांक**  **Sr. No** | **युनिट**  Unit | **संघटक**  Constituent/  IPP | **क्षमता मेगावॉट**  Cap.MW/kV | **से**  From  **समय दिनांक** | | **से**  To  **समय दिनांक** | | **कारण**  Reason |
|  |  |  |  | **Time** | **Date** | **Time** | **Date** |  |
|  | 400KV-ATHENA-Raigarh-1 | ACPL | 400KV | 22:02 | 30-04-2016 | Still out | Still out | Y-PH df/dt relay operatec at Athena; provision of df/dt relay at Athena and settings are being checked by Athena/ Kept out after FTC |
|  | 400KV-ATHENA-Raigarh-2 | ACPL | 400KV | 11:46 | 01-05-2016 | Still out | Still out | FOR TESTING AND CHECKING WORKS/ Kept out after FTC |
|  | 400KV-Raigarh-RAIPUR-2 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 07:48 | 06-07-2016 | Still out | Still out | DUE TO FIRE AT TCSC |
|  | 400KV-Raigarh-RAIPUR-1 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 08:42 | 08-07-2016 | Still out | Still out | main control system computer failure |
|  | 400KV-CHANDRAPUR-GCR-PARLI-M-3 L/R@ CHANDRAPUR-GCR - 400KV | Maharashtra | 400KV | 00:00 | 21-09-2016 | Still out | Still out | LR Faulty, Under Repairining |
|  | 1200KV/400KV BINA-ICT-2 | POWERGRID-WR2 (PGCIL) | 1200KV/400KV | 06:31 | 12-03-2017 | Still out | Still out | BUCHHHOLTZ OPERATED |
|  | KORBA(E) - UNIT 1 | Chattisgarh | 50.0 | 21:46 | 06-08-2017 | Still out | Still out | Water wall tube leakage |
|  | KORBA(E) - UNIT 2 | Chattisgarh | 50.0 | 20:53 | 23-10-2017 | Still out | Still out | Mill fan problem |
|  | PADGHE - 400KV B/R 1 | Maharashtra | 400KV | 00:00 | 13-01-2018 | 16:35 | 25-09-2020 | Bushing tan delta high. |
|  | 400KV-RAIPUR-Wardha-1 FSC@ Wardha | POWERGRID-WR1 (PGCIL) | 400KV | 14:04 | 01-02-2018 | Still out | Still out | A/R Operated successfully at both end; Damping resistor burnt |
|  | 400KV/220KV SATPURA-ICT-1 | Madhya Pradesh | 400KV/220KV | 21:53 | 19-04-2018 | Still out | Still out | differential protection operated |
|  | KORBA(E) - UNIT 3 | Chattisgarh | 50.0 | 12:42 | 12-09-2018 | Still out | Still out | Super heater problem |
|  | KORBA(E) - UNIT 4 | Chattisgarh | 50.0 | 15:46 | 14-09-2018 | Still out | Still out | Outage of coal mill |
|  | BHUSAWAL - 400KV B/R 1 | Maharashtra | 400KV | 13:49 | 10-11-2018 | Still out | Still out | Caught fire |
|  | 400KV/220KV PADGHE-ICT-1 | Maharashtra | 400KV/220KV | 10:07 | 15-11-2018 | Still out | Still out | Differential protection operated on LV side |
|  | 400KV-RAIPUR-Wardha-2 FSC@ Wardha | POWERGRID-WR1 (PGCIL) | 400KV | 14:12 | 17-11-2018 | Still out | Still out | Tripped along with the line; line tripped on fault;As intimated by RTAMC During dissipation of surge energy of fault during AR, the Damping resistor, IPS tube connectors to Damping resistor, cables to trigatron circuit of Raipur FSC#2 was damaged. |
|  | WPCL - UNIT 1 | Maharashtra | 135.0 | 04:48 | 25-11-2018 | Still out | Still out | No PPA |
|  | GPEC - UNIT 4 | Gujarat | 241.0 | 16:36 | 06-12-2018 | Still out | Still out | High pressure control valve problem |
|  | DHARIWAL - 400KV B/R 1 | Dhariwal-STU (DIL) | 400KV | 08:21 | 12-04-2019 | Still out | Still out | differential PROTECTION OPERATED. |
|  | BABLESHWAR - 400KV B/R 2 | Maharashtra | 400KV | 19:12 | 26-06-2019 | Still out | Still out | Failure of Bushing due to which Bus Reactor caught fire |
|  | 400KV-PARLI-M-LONIKHAND-II-2 L/R@ LONIKHAND-II - 400KV | Maharashtra | 400KV | 18:47 | 02-10-2019 | Still out | Still out | completion of its life and deviation of its parameters |
|  | 400KV/132KV VINDHYACHAL-ICT-1 | NTPC | 400KV/132KV | 10:40 | 13-10-2019 | Still out | Still out | due to 200MVA ICT-I got fire bus-3 bus bar protection operated |
|  | 765KV-DHULE-KHANDWA-1 L/R@ DHULE - 765KV | BDTCL-Sterlite | 765KV | 16:42 | 22-10-2019 | Still out | Still out | PRV-1 operated. |
|  | NASIK - UNIT 5 | Maharashtra | 210.0 | 10:25 | 12-12-2019 | Still out | Still out | PA Fan problem (Under Case 4 Bidding from 04.25Hrs DT. 13-12-2019) |
|  | 400KV-VADINAR-BACHAU-2 | POWERGRID-WR2 (PGCIL) | 400KV | 16:00 | 17-12-2019 | Still out | Still out | Manually opened due to High Voltage / MOHV |
|  | 400KV-Raigarh-RAIPUR-4 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 22:09 | 01-02-2020 | Still out | Still out | Voltage Regulation / VR |
|  | 400KV-Raigarh-RAIPUR-3 FSC@ RAIPUR | POWERGRID-WR1 (PGCIL) | 400KV | 22:11 | 01-02-2020 | Still out | Still out | Voltage Regulation / VR |
|  | NASIK - UNIT 3 | Maharashtra | 210.0 | 00:00 | 17-02-2020 | Still out | Still out | CW Pump high vibration |
|  | Satpura II - UNIT 4 | Madhya Pradesh | 210.0 | 02:52 | 22-02-2020 | Still out | Still out | BTL |
|  | Uran - UNIT 8 | Maharashtra | 108.0 | 20:57 | 01-03-2020 | Still out | Still out | Gas shortage |
|  | 400KV-SAGAR-SATNA-1 L/R@ SAGAR - 400KV | Madhya Pradesh | 400KV | 01:24 | 04-03-2020 | Still out | Still out | Hand Tripped after testing of first time charging. |